- requirement

| ITEM | DESCRIPTION | QTY | UNIT |
| --- | --- | --- | --- |
| 1 | Check valve : 6” , 300#, built in dual plate Wafer type , body ASTMA216 WCB, disc A351 CF8, stern A182 F304, spring is stainless steel, rubber gasket is PTFE, Design and manufacture standard :API 6D | 10 | EA |
| 2 | Check valve : 4” , 300#, built in dual plate Wafer type , body and plate ASTMA216 WCB, disc A351 CF8, stern A182 F304, spring is stainless steel, rubber gasket is PTFE, Design and manufacture standard :API 6D | 10 | EA |
| 3 | Safety valve: Spring full lift, Inlet 3"x300# RF, Outlet 4"x150# RF, Flange standard is ANSI B 16.5 ,body and bonnet WCB, Disc/guide/stem 316SS, metal to non-metal seated, seal seated is PTFE, set pressure is 7 kg/cm2. application liquid is fire water, design and manufacture: API RP 520, test and inspection: API 527. ( For the discharge of fire fighting pump) | 10 | EA |
| 4 | Safety valve : Spring full lift, inlet 3"x300# RF, outlet 4"x150# RF, Flange connection standard is ANSI B16.5, body and bonnet WCB, Disc/guide/stem 316SS,metal to non-metal seated, seal seated is PTFE, set pressure is 18 kg/cm2. Application liquid is crude oil, operation temperature is below 120 °C. design and manufacture: API RP 520, test and inspection: API 527. ( For test seperator, please refer to attached data sheet). | 8 | EA |
| 5 | Safety valve: Spring full lift, inlet 4"x300# RF, outlet 6"x150# RF, Flange connection standard is ANSI B16.5, body and bonnet WCB, Disc/guide/stem 316SS,metal to non-metal seated, seal seated is PTFE, set pressure is 18 kg/cm2. Application liquid is crude oil, operation temperature is below 120 °C. design and manufacture: API RP 520, test and inspection: API 527. (For 1st and 2nd seperator, please refer to data sheet) | 8 | EA |
| 6 | Safety valve: Spring full lift, inlet 6"x300# RF, outlet 8"x150# RF, Flange connection standard is SNSI B16.5, body and bonnet WCB, Disc/guide/stem 316SS,metal to non-metal seated, seal seated is PTFE, set pressure is 4 kg/cm2. Application liquid is crude oil, operation temperature is below 120 °C. design and manufacture: API RP 520, test and inspection: API 527. ( For 3rd seperator, please refer to the attached data sheet). | 8 | EA |
| 7 | Basket filter 6" x300#, flange connection, RF, Standard is ANSI B16.5, Max. pressure 16 bar, body CS, the filter core is SS316, two | 8 | EA |

type, one is 40 Mesh , and another type is 60 Mesh.	with 10 spare filter cores for each type. (please refer to the drawing of basket filter)

Note:

  - More technical information please refer to the attachment as below: Attachment 1-Data sheet for PSV rev.01

Attachment 2-Basket filter： DN150 Model

2, All the valves should be follow API standard, check valve is followed API 6D, Safety valve is followed API 520. Supplier must submit data sheet for approval if the goods is deviation with the requirement.