您好，

这是坦桑尼亚政府的一个采购竞标工程，真诚希望可以和贵司合作。

现在我们要先给客户报价，请仔细看下面的要求: 

以下有生产标准、质量检测、包装、材料属性、工厂要提供的文件、数量和具体的细节参数要求，请贵司务必要严格按照文件的要求，来报价格

CIF价格、图片、起订量、交货日期、包装方式等。

1. 首先是否有这个资质做这批货，特别是DOCUMENT.

2. 确定是否可以严格按照下面的技术参数做这个货。

3. 如果可以做，请贵司报CIF价格 目的地达累斯萨拉姆，同时也给出含税运的工厂价（到宁波），以上内容报价内容连同ISO证书，请贵司于周二晚上之前发给我。

4. 请留好负责人的电话和邮箱，我们随时要保持联系。

祝商祺

王辉

15728023893

邮箱：woaiwojia559@163.com
Lot 4: Distribution line hardware
	Line Item

N(
	Description of Goods 
	Quantity 
	Physical unit
	Final (Project Site) Destination as specified in BDS*
	Delivery Date

	
	
	
	
	
	Latest Delivery Date 
	Bidder’s  offered Delivery date [to be provided by the bidder] 

	1
	Oval eye nut, M16, galvanized, strength of Grade 4.6 bolt
	3,600
	ea.
	Kilombero district
	20 weeks
	

	2
	Nut, thimble type eye, M16
	600
	ea.
	Kilombero district
	20 weeks
	

	3
	Galvanized ground rod 16mm dia, 2400mm long
	6,900
	ea.
	Kilombero district
	20 weeks
	

	4
	ground rod clamp for 16mm dia ground rod
	7,000
	ea.
	Kilombero district
	20 weeks
	

	5
	Staples, ground wire
	24,700
	ea.
	Kilombero district
	20 weeks
	

	6
	Straight,thimble eyebolt, M16x250 Grade 4.6
	800
	ea.
	Kilombero district
	20 weeks
	

	7
	Wire holder clevis type
	6,200
	ea.
	Kilombero district
	20 weeks
	

	8
	Anchor Shackle, 70kN, straight, pin type
	3,900
	ea.
	Kilombero district
	20 weeks
	

	9
	Single upset Bolt M16x250mm Grade 4.6
	6,800
	ea.
	Kilombero district
	20 weeks
	

	10
	Preformed Armor rods for single support for Shrike Conducstor
	0
	ea.
	Kilombero district
	20 weeks
	

	11
	Preformed Armor rods for single support Gopher conductor
	500
	ea.
	Kilombero district
	20 weeks
	

	11
	Preformed Armor rods for single support Rabbit conductor
	1,000
	ea.
	Kilombero district
	20 weeks
	

	12
	Preformed Armor rods for single support Hare conductor
	1,550
	ea.
	Kilombero district
	20 weeks
	

	13
	Preformed Armor rods for double support for Shrike conductor
	0
	ea.
	Kilombero district
	20 weeks
	

	14
	Preformed Armor rods for double support for Gopher conductor
	300
	ea.
	Kilombero district
	20 weeks
	

	15
	Preformed Armor rods for double support Rabbit conductor
	400
	ea.
	Kilombero district
	20 weeks
	

	16
	Preformed Armor rods for double support Hare conductor
	650
	ea.
	Kilombero district
	20 weeks
	

	17
	Preformed Dead end for Shrike conductor
	0
	ea.
	Kilombero district
	20 weeks
	

	18
	Preformed Dead end for Gopher conductor
	700
	ea.
	Kilombero district
	20 weeks
	

	19
	Preformed Dead end for Rabbit conductor
	1,100
	ea.
	Kilombero district
	20 weeks
	

	20
	Preformed Dead end for Hare conductor
	1,900
	ea.
	Kilombero district
	20 weeks
	

	21
	Wedge type Service Deadend
	12,500
	ea.
	Kilombero district
	20 weeks
	

	22
	Service grip for Periwinkle conductor
	2,500
	ea.
	Kilombero district
	20 weeks
	

	23
	Bolt, machine M16 x 250 rolled threads, grade 4.6, galvanized with nut
	12,000
	ea.
	Kilombero district
	20 weeks
	

	24
	Bolt Machine M16 x 300mm, rolled threads, grade 4.6, galvanized, with nut
	1,500
	ea.
	Kilombero district
	20 weeks
	

	25
	Bolt, machine M16 x 350mm,  rolled threads, Grade 4.6, galvanized, with nut
	500
	ea.
	Kilombero district
	20 weeks
	

	26
	Bolt, machine M20 x 300mm,  rolled threads, Grade 4.6, galvanized, with nut
	500
	ea.
	Kilombero district
	20 weeks
	

	27
	Angle suspension clamp for angles up to 2x30 degrees, sized for use over armor rods
	400
	ea.
	Kilombero district
	20 weeks
	

	28
	Clevis-thimble for preformed deadend, 70kN
	3,600
	ea.
	Kilombero district
	20 weeks
	

	29
	Clamp, anchor rod for 16mm dia rod
	2,500 
	ea.
	Kilombero district
	20 weeks
	

	30
	Insulator, spool ANSI 53-2
	7,500 
	ea.
	Kilombero district
	20 weeks
	

	31
	Pair crossarm braces, 700mm long, 10mm and 12mm holes, wood center section
	4,200 
	ea.
	Kilombero district
	20 weeks
	

	32
	Round Washer, 50mmx 3mm 17mm hole
	1,000 
	ea.
	Kilombero district
	20 weeks
	

	33
	Washer, square 50x50x6mm, galvanized, 17mm hole, galvanized
	39,000 
	ea.
	Kilombero district
	20 weeks
	

	34
	Spool Insulator support
	7,500
	ea.
	Kilombero district
	20 weeks
	

	35
	Post Insulator ANSI 57-2, 160kV BIL, F-Neck, M16x 180mm stud, w nut
	5,000
	ea.
	Kilombero district
	20 weeks
	

	36
	Bracket, pole top for post insulator w M16 hardware
	1,500
	ea.
	Kilombero district
	20 weeks
	

	37
	Spring washers, M16
	35,000
	ea.
	Kilombero district
	20 weeks
	

	38
	Spring washers, M10
	15,000
	ea.
	Kilombero district
	20 weeks
	

	39
	Bolt, carriage 10mm x 115mm, galvanized
	8400
	ea.
	Kilombero district
	20 weeks
	

	40
	Lag screw, galvanized, M12 x 100mm, drive point
	4,200
	ea.
	Kilombero district
	20 weeks
	

	41
	Suspension insulator, clevis type, 254mm diam, 70kN M&E rated
	11,600
	ea.
	Kilombero district
	20 weeks
	

	42
	Bolt Double arming, M16 x 450mm Grade 4.6, rolled threads, galvanized, w 4 nuts ea.
	3,500
	ea.
	Kilombero district
	20 weeks
	

	43
	Bolt Double arming, M16 x 550mm Grade 4.6, rolled threads, galvanized, w 4 nuts ea.
	1,500
	ea.
	Kilombero district
	20 weeks
	

	44
	Bolt, oval eye, M16 x 250mm, Grade 4.6 rolled threads, galvanized
	6,500
	ea.
	Kilombero district
	20 weeks
	

	45
	Compression connectors, aluminum, H block, 35mm2/16mm2 to 35mm2/16mm2 
	6,000
	ea.
	Kilombero district
	20 weeks
	

	46
	Compression connectors, aluminum, H block, 50mm2 to 25mm2/16mm2 
	700
	ea.
	Kilombero district
	20 weeks
	

	47
	Compression connectors, aluminum, H block, 100mm2 to 25mm2 
	700
	ea.
	Kilombero district
	20 weeks
	

	48
	Compression connectors, aluminum, H block, 50mm2 to 50mm2
	500
	ea.
	Kilombero district
	20 weeks
	

	49
	Compression connectors, aluminum, H block, 100mm2 to 50mm2
	100
	ea.
	Kilombero district
	20 weeks
	

	50
	Compression connectors, aluminum, H block, 100mm2 to 100mm2
	500
	ea.
	Kilombero district
	20 weeks
	

	51
	Single hole compression lug with 12mm hole for transformer stud and two set screw connectors for 25mm2 Al cable
	2,000
	ea.
	Kilombero district
	20 weeks
	

	52
	Formed wire stay grip for 7x3.35mm (3/8'') EHS galvanized stay wire
	5,300
	ea.
	Kilombero district
	20 weeks
	

	53
	Formed wire stay grip for 7x2mm (1/4'') EHS galvanized stay wire
	650
	ea.
	Kilombero district
	20 weeks
	

	54
	Guy attachment
	2,400
	ea.
	Kilombero district
	20 weeks
	

	55
	Staywire insulator ANSI 54-3, 69kN RBS
	2,200
	ea.
	Kilombero district
	20 weeks
	

	56
	Anchor Rod, thimble eye M16x2400mm
	2,400
	ea.
	Kilombero district
	20 weeks
	

	57
	Anchor cross plate type 1600 cm2
	2,200
	ea.
	Kilombero district
	20 weeks
	

	58
	Cable Tie 21" Black Nylon UV
	15,000
	ea.
	Kilombero district
	20 weeks
	

	59
	Ground wire,  soft annealed iron, 3 strand x 4mm galvanised
	26,500
	meter
	Kilombero district
	20 weeks
	

	60
	7x 2 mm (1/4" EHS)  staywire
	5,000
	meter
	Kilombero district
	20 weeks
	

	61
	Staywire 7x 3.35mm dia, 69kN RBS, Galvanized Class C
	40,000
	meter
	Kilombero district
	20 weeks
	


1 Technical Specification: Distribution Line Hardware

1.1 Scope

This specification shall cover the design, manufacturing, testing and supply of distribution line hardware and accessories for installation on rural distribution lines in Tanzania.

1.2 Standards

The materials offered shall conform to the latest editions of the ANSI, NEMA, IEC and ISO standards applicable to their construction.

1.3 Experience and Quality Control

The materials supplied under this RFQ shall be fabricated in a plant that has manufactured materials of similar ratings and characteristics for a period of not less than ten years, and that holds an ISO 9001:2008 certification for quality management.

1.4 Material Characteristics

Hardware and accessories shall comply to the specifications provided by TANESCO.  Bidder may substitute technically equivalent materials fabricated by other manufacturers, if qualified on the basis of experience, quality control, source, and origin requirements of the RFQ.  
1.5 Packaging

All materials supplied under this contract shall be packaged in sealed ocean freight containers for export to a tropical climate, and shall be packed in such a fashion as to be protected from conditions that may occur during loading, transport and unloading without suffering damage.  The packaging shall comply with the best commercial practice for these conditions.  Packaging for materials subject to deterioration on exposure to weather shall be sufficient to protect them from these conditions both during transit and during outdoor storage for a period not less than two months.

Minimum protection for those materials packed in cardboard boxes shall be palletizing of the boxes on a wooden pallet, protected and sealed with an integral plastic wrapping that not only covers the entirety of the packaged materials, but which also protects the interior from moisture entry.

Unless otherwise specified, steel guy strand and ground wire shall be supplied in 200 meter coils, subject to the length tolerances specified by the applicable standard.

1.6 Documentation

The following technical information shall be provided with the tender for each item offered:

· Description of the materials supplied including evidence of compliance with referenced standards and equivalence to descriptions and reference manufacturers listed in Quotation Tables

· Packaging details.

· Terms of manufacturer’s warranty

· Statement of manufacturing experience of plant where conductors will be manufactured

· Statement of country of origin for all items

· List and explanations for any deviations from or exceptions to these specifications

· Copy of ISO 9001:2008 certifications for the manufacturing plant

1.7 Technical Particulars for Distribution Line Accessories

Guarantee Schedules (G-12):Technical Data for Line Hardware and Accessories
Equivalent Reference Catalog for distribution line hardware technical specifications. Bidders are required to compete the following by entering the manufacturer and catalog number of the proposed TANESCO Technical specifications:-
1. Specification S12 - Staywire and Stay Accessories
2. Specification S13 - Crossarms and Associated Steelwork
3. Specification S14 – Insulators
4. Specification S15 –Line Fittings
5. Specification S19 - Line Binding Accessories
6. Specification S30 - LV Service Cable
7. Specification S33 - Lv house service cut
8. Specification S35 - Bolts, Nuts and Washers
9. Specification S36 - Warning and Identification Plates
10. Specification S56 - Power Cable Connectors
Technical specifications for distribution line Accessories

	Sl#
	Materials
	Ref. 

Code
	 

Unit
	Bidder Offer 

	
	
	
	
	Mfr.
	Catalog No.

	1
	Oval eye nut, M16, galvanized, strength of Grade 4.6 bolt
	aa
	ea.
	
	

	2
	Nut, thimble type eye, M16
	ab
	ea.
	
	

	3
	Surge Arrester, gap type MOV, polymer housed,  36kV UR, 29kV UC normal duty with crossarm bracket and isolator
	ae
	ea.
	
	

	4
	Fused cutout, 100amp,  27kV, 170kV BIL, 10kA, with crossarm bracket for 90x 115mm crossarm
	af
	ea.
	
	

	5
	Galvanized ground rod 16mm dia, 2400mm long
	ai
	ea.
	
	

	6
	ground rod clamp for 16mm dia ground rod
	aj
	ea.
	
	

	7
	Staples, ground wire
	al
	ea.
	
	

	8
	Straight,thimble eyebolt, M16x250 Grade 4.6
	ao
	ea.
	
	

	9
	Wire holder clevis type
	ar
	ea.
	
	

	10
	Anchor Shackle, 70kN, straight, pin type
	bo
	ea.
	
	

	11
	Single upset Bolt M16x250mm Grade 4.6
	bs
	ea.
	
	

	12
	Preformed Armor rods for single support for Shrike Conducstor
	bv
	ea.
	
	

	13
	Preformed Armor rods for single support Gopher conductor
	bv
	ea.
	
	

	14
	Preformed Armor rods for single support Rabbit conductor
	bv
	ea.
	
	

	15
	Preformed Armor rods for single support Hare conductor
	bv
	ea.
	
	

	16
	Preformed Armor rods for double support for Shrike conductor
	bv
	ea.
	
	

	17
	Preformed Armor rods for double support for Gopher conductor
	bv
	ea.
	
	

	18
	Preformed Armor rods for double support Rabbit conductor
	bv
	ea.
	
	

	19
	Preformed Armor rods for double support Hare conductor
	bv
	ea.
	
	

	20
	Preformed Dead end for Shrike conductor
	by
	ea.
	
	

	21
	Preformed Dead end for Gopher conductor
	by
	ea.
	
	

	22
	Preformed Dead end for Rabbit conductor
	by
	ea.
	
	

	23
	Preformed Dead end for Hare conductor
	by
	ea.
	
	

	24
	Wedge type Service Deadend 
	by
	ea.
	
	

	25
	Service grip for Periwinkle conductor
	by
	ea.
	
	

	26
	Bolt, machine M16 x 250 rolled threads, grade 4.6, galvanized with nut
	c
	ea.
	
	

	27
	Bolt Machine M16 x 300mm, rolled threads, grade 4.6, galvanized, with nut
	c
	ea.
	
	

	28
	Bolt, machine M16 x 350mm,  rolled threads, Grade 4.6, galvanized, with nut
	c
	ea.
	
	

	29
	Bolt, machine M16 x 400mm,  rolled threads, Grade 4.6, galvanized, with nut
	c
	ea.
	
	

	30
	Angle suspension clamp for angles up to 2x30 degrees, sized for use over armor rods
	cd
	ea.
	
	

	31
	Clevis-thimble for preformed deadend, 70kN
	ci
	ea.
	
	

	32
	Clamp, anchor rod for 16mm dia rod
	ck
	ea.
	
	

	33
	Insulator, spool ANSI 53-2
	cm
	ea.
	
	

	34
	Pair crossarm braces, 700mm long, 10mm and 12mm holes, wood center section
	cu
	pair
	
	

	35
	Round Washer, 50mmx 3mm 17mm hole
	d
	ea.
	
	

	36
	Washer, square 50x50x6mm, galvanized, 17mm hole, galvanized
	d
	ea.
	
	

	37
	Spool Insulator support
	da
	ea.
	
	

	38
	Post Insulator ANSI 57-2, 160kV BIL, F-Neck, M16x 180mm stud, w nut
	ea
	ea.
	
	

	39
	Bracket, pole top for post insulator w M16 hardware
	eb
	ea.
	
	

	40
	Spring washers, M16
	ek
	ea.
	
	

	41
	Spring washers, M10
	ek
	ea.
	
	

	42
	Bolt, carriage 10mm x 115mm, galvanized
	i
	ea.
	
	

	43
	Lag screw, galvanized, M12 x 100mm, drive point
	j
	ea.
	
	

	44
	Suspension insulator, clevis type, 254mm diam, 70kN M&E rated
	k
	ea.
	
	

	45
	Bolt Double arming, M16 x 450mm Grade 4.6, rolled threads, galvanized, w 4 nuts ea.
	n
	ea.
	
	

	46
	Bolt Double arming, M16 x 550mm Grade 4.6, rolled threads, galvanized, w 4 nuts ea.
	n
	ea.
	
	

	47
	Bolt, oval eye, M16 x 250mm, Grade 4.6 rolled threads, galvanized
	o
	ea.
	
	

	48
	Compression connectors, aluminum, H block,  35mm2/16mm2 to 35mm2/16mm2 
	p
	ea.
	
	

	49
	Compression connectors, aluminum, H block, 50mm2 to 25mm2/16mm2 
	p
	ea.
	
	

	50
	Compression connectors, aluminum, H block, 100mm2 to 25mm2 
	p
	ea.
	
	

	51
	Compression connectors, aluminum, H block, 50mm2 to 50mm2
	p
	ea.
	
	

	52
	Compression connectors, aluminum, H block, 100mm2 to 50mm2
	p
	ea.
	
	

	53
	Compression connectors, aluminum, H block, 100mm2 to 100mm2
	p
	ea.
	
	

	54
	Single hole compression lug with 12mm hole for transformer stud and two set screw connectors for 25mm2 Al cable
	p1
	ea.
	
	

	55
	Formed wire stay grip for 7x3.35mm (3/8'') EHS galvanized stay wire
	u
	ea.
	
	

	56
	Formed wire stay grip for 7x2mm (1/4'') EHS galvanized stay wire
	u
	ea.
	
	

	57
	Guy attachment
	v
	ea.
	
	

	58
	Staywire insulator ANSI 54-3, 69kN RBS
	w
	ea.
	
	

	59
	Anchor Rod, thimble eye M16x2400mm
	x
	ea.
	
	

	60
	Anchor cross plate type 1600 cm2
	z
	ea.
	
	

	61
	Cable Tie 21" Black Nylon UV
	 
	ea.
	
	

	62
	Ground wire,  soft annealed iron, 3 strand x 4mm galvanised 
	cj
	mtr
	
	

	63
	7x 2 mm (1/4" EHS)  staywire
	y
	mtr.
	
	

	64
	Staywire 7x 3.35mm dia, 69kN RBS, Galvanized Class C
	y
	mtr.
	
	


Guarantee Schedules (G-13):Technical Data for Surge Arrester, 33 kV
	Technical Data for Surge Arrester, 33 kV

	No.
	Description 
	Minimum Requirements 
	Data offered by Bidder 

	
	
	Unit
	Data
	

	1
	Manufacturer
	
	 
	 

	2
	Country of origin
	
	 
	 

	3
	Type
	
	polymer housed, gap type
	 

	4
	Housing
	
	composite Polymeric housing
	 

	5
	Color
	
	grey
	 

	
	Nominal characteristics
	
	 
	 

	6
	Temp. Overvoltage for 10s.
	p.u. MCOV
	2.0
	 

	7
	Rated operating voltage Ur
	kV rms
	36
	 

	8
	Max. continuous operating voltage Uc
	kV rms
	29
	 

	9
	Rated discharge current (peak)
	kA
	5
	 

	10
	Line discharge class (IEC 60099-4)
	
	1
	 

	11
	ANSI Duty rating
	
	Normal
	

	12
	Rated frequency
	Hz
	50
	 

	
	Protection characteristics
	
	 
	 

	14
	Max. residual voltages:
	
	 
	 

	
	 For lightning impulse current, 8/20 µs, 5 kA
	kV
	80
	 

	
	Insulation levels of Housing
	
	 
	 

	15
	Lightning impulse withstand voltage of housing
	kV
	200
	 

	16
	Power frequency withstand (10 sec wet)
	kV
	140
	 

	17
	Power frequency withstand volt. (1 min. dry)
	
	148
	 

	18
	Creepage distance
	mm
	1000 
	 

	
	Weights and dimensions
	
	 
	 

	19
	· Outline drawing
	
	To be supplied by Bidder-
	 

	20
	· Weight
	kg
	To be supplied by Bidder-
	 

	
	Accessories
	
	 
	 

	21
	Mounting hardware
	
	yes
	 

	22
	Crossarm Bracket- wood crossarm 90x115mm
	
	yes
	

	23
	Isolator
	
	yes
	

	24
	Ground connector
	Type
	Stud and wire clamp
	 

	25
	HV terminals connectors
	Type
	Stud and wire clamp
	 

	26
	Type test report
	
	to be included in bid
	 

	27
	Standard(s)
	
	IEC 60099-4 or ANSI C62.11
	 

	38
	Quality control
	
	ISO 9001
	 

	29
	Installation
	
	outdoor
	 


Guarantee Schedules (G-14):Technical Data for Fuse Cut-Out, 33 kV
	Technical Data for Fuse Cut-Out, 33 kV

	No.
	Description 
	Minimum Requirements 
	Data offered by Bidder 

	
	
	Unit
	Data
	

	1
	Manufacturer
	
	 
	 

	2
	Country of origin
	
	 
	 

	3
	Type
	
	
	 

	4
	Rated max. voltage
	
	
	 

	
	· Phase to ground
	kV
	27
	 

	5
	Rated current
	A
	100
	 

	6
	Rated frequency
	Hz
	50
	 

	7
	Asymmetrical interrupting current
	kA
	10
	

	8
	Impulse withstand voltage BIL
	kV
	170
	 

	9
	Power frequency withstand voltage
	kV(rms)
	70 
	 

	10
	Creepage distance 
	mm/kV
	25
	 

	11
	Max. ambient temperature
	°C
	40 
	 

	13
	Bushing type
	
	porcelain
	

	14
	Fuse holder cap compatible with universal fuse links
	
	yes
	

	15
	Max. relative humidity
	%
	90 
	 

	16
	Mounting crossarm bracket meeting the requirements of ANSI C37.42, Section 2.4 for Type A mounting brackets. The mounting bracket shall be adjustable to accommodate standard 90*115 * 2400 meter wood cross arms.
	
	yes
	 

	17
	Terminals can be connected with aluminum /copper cables
	
	yes
	 

	18
	Standard
	
	IEC /NEMA IEEE-C37.40 ANSI37.42
	


Guarantee Schedules (G-15):Technical Data for 33 kV Porcelain Post Insulator ANSI 57-2, 180kV BIL, F-Neck, M16x 180mm stud, w nut
	Technical Data for 33 kV Porcelain Post Insulator

	No.
	Description
	Minimum Requirements 
	Data offered by Bidder 

	
	
	Unit
	Data
	

	1
	Manufacturer
	
	
	

	2
	Country of  Origin
	
	
	

	3
	Type
	
	Post Insulator ANSI 57-2, F-Neck
	

	4
	Material
	
	Porcelain
	

	5
	Rated voltage
	kV
	35
	

	6
	Low frequency flashover voltage:
	
	 
	

	
	· Dry
	kV
	110
	

	
	· Wet
	kV
	85
	

	7
	Impulse flashover voltage:
	
	 
	

	
	· Positive
	kV
	180
	

	
	·  negative
	kV
	205
	

	8
	Mechanical tensile load "T"
	kN
	to be provided by Bidder
	

	9
	Mechanical cantilever load "F"
	kN
	to be provided by Bidder
	

	10
	Nominal diameter "D"
	mm
	to be provided by Bidder
	

	11
	Maximum height "H"
	mm
	to be provided by Bidder
	

	12
	Leakage distance 
	mm
	571
	

	13
	Dry arching distance 
	mm
	241
	

	14
	Unit weight
	kg
	to be provided by Bidder
	

	15
	M16x 180mm stud, with nut
	
	yes 
	

	16
	Standard(s)
	
	ANSI CLASS (C29.7-1996 rev. 2002) 57-2
	


Guarantee Schedules (G-16):Technical Data for 33 kV Porcelain Suspension Insulator, 70kN, U70BL
	Technical Data for 33 kV Porcelain Suspension Insulator

	No.
	Description
	Minimum Requirements 
	Data offered by Bidder 

	
	
	Unit
	Data
	

	1
	Manufacturer
	
	
	 

	2
	Country of Origin
	
	
	

	3
	Type
	
	   IEC U70BL
	 

	4
	Catalogue No..
	
	
	

	5
	Material
	
	Porcelain
	 

	6
	Rated voltage
	kV
	36
	 

	7
	Minimum mechanical failing load
	kN
	70
	 

	8
	Power frequency withstand voltage:
	
	
	 

	
	·  Dry
	kV
	170
	 

	
	· Wet
	kV
	70
	 

	9
	Dry impulse withstand voltage (positive and negative):
	kV
	100
	 

	10
	Disc diameter
	mm
	to be provided by Bidder
	 

	11
	Minimum nominal creepage distance
	mm
	to be provided by Bidder
	 

	12
	Number of elements
	no.
	to be provided by Bidder
	 

	13
	Ball and socket coupling size 
	mm
	to be provided by Bidder
	 

	14
	Stainless steel split pin size
	
	to be provided by Bidder
	 

	15
	Weight
	kg
	to be provided by Bidder
	 

	16
	With all necessary accessories for installation 90x115x24000mm crossarm
	
	 
	 

	17
	Standard(s)
	
	IEC383
	 


