## Sheet1 (hidden)
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
1 | 自动软化水处理器AUTOMATIC DECALCIFIER |  |  | 型号MODEL：ECB 最大流量Maximum Flow ：1500l/h 电气性能Electric characteristics ：220V/50Hz 最大运行压力Maximum Operation Pressure： 7Kg/cm 2 最小运行压力Minimum Operation Pressure： 2Kg/cm 2 容量Capacity： 80 L | 合格qualified | CE | 台un | 1 | 参考品牌Reference Brand or Equivalent：ERIE / ENKROTT 空调软化水处理成套设备，参看空调图纸， 供应商予以深化并提供具体参数和安装尺寸 demineralized water treatment equipment for air conditioning system， see air-conditioning drawings to be deepen by suppliers ,and provide specific parameters and installation dimensions
2 | 计量表 DOSING AREA |  |  | 型号MODEL： DMREVRO 流量Flow Rate： 2 a 11 l/h 电气性能Electric characteristics： 380V/50Hz 最大运行压力Maximum Operation Pressure ：7.5Kg/cm 2 脉动频率Pulsation Frequence：120 pm | 合格qualified | CE | 台un | 1 | 参考品牌Reference Brand or Equivalent：ERIE / ENKROTT 空调软化水处理成套设备，参看空调图纸， 供应商予以深化并提供具体参数和安装尺寸 demineralized water treatment equipment for air conditioning system， see air-conditioning drawings to be deepen by suppliers ,and provide specific parameters and installation dimensions
3 | 计量泵 DOSING PUMP |  |  | 型号MODEL： DMREVRO 流量Flow Rate ：2 a 11 l/h 电气性能Electric characteristics： 380V/50Hz 最大运行压力Maximum Operation Pressure： 7.5Kg/cm 2 脉动频率Pulsation Frequence：120 pm ~ 容量Capacity： 110 L | 合格qualified | CE | 台un | 1 | 参考品牌Reference Brand or Equivalent：ERIE / ENKROTT 空调软化水处理成套设备，参看空调图纸， 供应商予以深化并提供具体参数和安装尺寸 demineralized water treatment equipment for air conditioning system， see air-conditioning drawings to be deepen by suppliers ,and provide specific parameters and installation dimensions
4 | 静态空气及污垢分离器Static TYPE AIR AND DIRT SEPARATORS | SAP–F | DN250 | 最大压力Max Pressure [bar]： 10 水流量Water Flow Rate [m3/h] ：1684 | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：SPIROVENT / CALEFFI 用于制冷回水管路Cooling Circuit (Return)， 供应商予以深化并提供具体参数和安装尺寸 Ror Cooling Circuit (Return), Supplier Deepens the drawings and Provide Specific Parameters and Mounting Dimensions
5 | 静态空气及污垢分离器Static TYPE AIR AND DIRT SEPARATORS | SAP–Q | DN125 | 最大压力Max Pressure [bar]： 10 水流量Water Flow Rate [m3/h] ：540 | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：SPIROVENT / CALEFFI 参看空调图纸，用于制冷回水管路Cooling Circuit (Return) ，供应商予以深化并提供具体参数和安装尺寸Ror Cooling Circuit (Return), Supplier Deepens the drawings and Provide Specific Parameters and Mounting Dimensions
6 | 氯化水处理器集成CHLORINE DOSING TREATMENT OF WATER |  |  | 水处理设备，有完整的氯/ pH值控制器，具有流量检测计。有消毒剂存储罐及计量泵，配电气控制箱和减振基础。配电箱预留楼宇自控BMS的通信接口Water treatment equipment,Complete chlorine/pH controller with flow detector.Complete chlorine/pH controller with flow detector.Dosing pump (disinfectant).Deposits tanks (disinfectant).Electrical-control panel. In coodination with BMS installations needs Electrical and control installation included。 | 合格qualified | CE | 台un | 1 | 参考给水图纸，供应商予以深化，并提供氯化水处理器集成相关参数和安装图纸Reference to the water supply drawings, to be deepened by suppliers， and provide chlorinated water processor integration related parameters and installation drawings
7 | 氯化水循环泵集成WATER RECIRCULATION PUMPING SYSTEM |  |  | 流量Q=4 l/s,扬程 HM= 12.00 m，几何压头：4m ，最小压力：50 kPa ，持续负载损失：3m，功率：1.1 kW + 1.1kW 泵组成：一用一备 。包括控制配电柜及具有所有电气连接，报警系统，稳压液气罐，转换阀、不锈钢管道和抽吸和输送歧管，不锈钢集水器，金属支架， 减振基础 。所用水泵为变速泵。 Supply pumping Central flow Q=4 l/s,，HM=12 m, Geometric Head ：4 m，Minimum Pressure ： 50KPa，Continuous load loss ：3m。power：1.1 kW+1.1kW made up 1 groups + 1 reserve group, including command and control switchboard of groups with all the electrical connections, alarm system, hydropneumatic tank, switching valves and stainless steel conections, disassembly joints, sectioning valves, piping and suction and delivery manifolds in stainless steell. metallic bench, antivibration supports。 All pumps are variable speed | 合格qualified | CE | 台un | 1 | 参考型号/厂商Model/producer ：ETL 32-32-160 GB / KSB 参考给水图纸，供应商予以深化，并提供氯化水循环泵集成相关参数和安装图纸Reference to the water supply drawings to be deepened by suppliers ，and provide chlorinated water recirculation pumping integration related parameters and installation drawings
8 | 给水泵集成 SUPPLY WATER PUMPING SYSTEM |  |  | 流量Q=7 l/s,（同时系数 = 20%）， 扬程HM= 63.80 m, 几何压头：38.8m ，最小压力：100 kPa ，持续负载损失：15m，功率：2 x 4 kW + 4 kW 泵组成：2组+ 1个备用组，及两用一备。包括控制配电柜及具有所有电气连接，报警系统，稳压液气罐，转换阀、不锈钢管道和抽吸和输送歧管，不锈钢集水器，金属支架， 减振基础 。所用水泵为变速泵。 Supply pumping Central flow Q=7 l/s,（Simultaneity coefficient = 20% ），HM= 63,80 m, Geometric Head ：38,80 m，Minimum Pressure ： 100KPa，Continuous load loss ：15 m。power：2 x 4 kW + 4 kW made up 2 groups + 1 reserve group, including command and control switchboard of groups with all the electrical connections, alarm system, hydropneumatic tank, switching valves and stainless steel conections, disassembly joints, sectioning valves, piping and suction and delivery manifolds in stainless steell. metallic bench, antivibration supports。 All pumps are variable speed 。 | 合格qualified | CE | 台un | 1 | 参考型号/厂商Model/producer ：HU VP 3/1010 / KSB 参考给水图纸，供应商予以深化，并提供不锈钢给水泵集成的相关参数和安装图纸Reference to the water supply drawings to be deepened by suppliers ，and provide supply water stainless steel pumping integration related parameters and installation drawings
9 | 潜污泵submersible pump | PBD |  | 流量Q =6 l/s (同时系数Simultaneity coefficient = 26%) 扬程Hm =8 MCA, 几何压头 Geometric Head： 6 m 电机功率Motor Power[kW] ：1.8KW+1.8KW 最小压力Minimum Pressure ： 10 kPa 连续负载损失Continuous load loss： 1 m 组成：一用一备。 配置潜污泵液位控制配电箱，液位开关及连接防水线缆等必备配件composed by 1 submersible group + 1 submersible group reserve, installed in pumping well including auxiliary equipment (level switch, sectioning valves and discharge pipes, retention, screws, suction filter and other necessary accessories, electrical installations, Electrical switchboard, all connections included and all work and materials necessary for correct installation, everything according technical specifications. | 合格qualified | CE | 台un | 2 | 参考型号/厂商Model/producer ：Amarex NF 65-220/024 ULG – 195 / KSB 参考排污水图纸，供应商予以深化，配套供应配电箱、液位开关及连接用的防水电缆等必备附件Reference draining water drawings to be deepened by suppliers ,and provide matching distribution box, level switches and waterproof cables and other necessary accessories
10 | 二次加热回路变速管道泵SECONDARY HEATING CIRCUIT Variable Speed IN - LINE Pumps | BDQ |  | 水流量Water Flow [m 3 /h]：36 扬程 Head [m.w.c.]：20 电机功率Motor Power[kW] ：3.5 转速Speed ：可变速Variable 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 4 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 三用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
11 | 二次制冷回路变速管道泵SECUNDARY COOLING CIRCUIT Variable Speed IN - LINE Pumps | BDF |  | 水流量Water Flow [m 3 /h]：199.8 扬程 Head [m.w.c.]：20 电机功率Motor Power[kW] ：15 转速Speed ：可变速Variable 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 3 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 两用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
12 | 一次加热回路定速管道泵PRIMARY HEATING CIRCUIT Constant Speed IN - LINE Pumps | BPQ |  | 水流量Water Flow [m 3 /h]：54 扬程 Head [m.w.c.]：10 电机功率Motor Power[kW] ：2.5 转速Speed ：定速Constant 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 3 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 两用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
13 | 一次制冷回路定速管道泵PRIMARY COOLING CIRCUIT Constant Speed IN - LINE Pumps | BPF |  | 水流量Water Flow [m 3 /h]：168.4 扬程 Head [m.w.c.]：10 电机功率Motor Power[kW] ：7.5 转速Speed ：定速Constant 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 3 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 两用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
14 | 消防水泵集成 Fire pump integration |  |  | 设计流量：Q=34 L/s ( 122,40 m³/h )，扬程 HM=85m， 水泵功率45 kW + 45 kW + 2.1kw 泵组成： 两台泵+一台稳压泵。 主泵符合标准EN 12845,单级卧式离心泵，主泵一用一备，轴向吸水，径向压缩符合标准 DIN24255， not self-priming。可调叶轮机械密封，自润滑轴承，三相异步电动机，风扇冷却，满足DIN和IEC 标准。 辅助稳压泵多级立式离心屏蔽泵，铸铁联轴器，，可调叶轮机械密封，自润滑轴承，三相异步电动机，风扇冷却，满足DIN和IEC 标准。参考型号。 消防电气控制箱QEP-1EAC ，金属材质，防护等级IP54，RAL3020 红色,接收并能发出24V电的信号指令，能自动启泵，手动停泵，具有消防泵远程启动/停止的接口端子并做好标记，其它标准组件，满足 EN 12845要求和葡萄牙规范。提供安装及操作说明书，泵站组件图，水泵性能曲线图，工厂调试合格证书。 具备消防电气集成控制箱，电气报警装置及各泵的连接线、控制线，电接点压力表，安全阀，气液膜式稳压罐，泵开关，泵口软连接，不锈钢连接管、带盲板法兰的分水器，甘油浴压力表，止回阀，薄膜流量计，正确执行消防水灭火任务所必须的内部连接件以及铸铁GG25.减振底板基础。Supply pumping Central FLOW Q=34 L/s = 122,40 m³/h to the distribution network of fire network system, made up of 2 pump groups + 1 auxiliar pump, model EDS EC 120-85 JEE / KSB , including command and control switchboard of groups with all the electrical connections, alarm system, hydropneumatic tank, switching valves and stainless steel conections, disassembly joints, piping and suction and delivery manifolds in stainless steell. Float slab, connections (hydraulic, electrical, control, fire etc) and derivation and all materials and work needed to perfect operation as technical specifications. Technical requirements, manufacturer and other construction detail according to specifications and drawings provided. | 合格qualified | CE | 台un | 1 | 参考型号/厂商Model/producer: EDS EC 120-85 JEE / KSB 参考消防水图纸，供应商予以深化，并提供相关泵组详细参数和安装图纸Reference fire water drawings to be deepened by suppliers, and provide the relevant pump group detailed parameters and installation drawings
15 | 湿式报警阀组集成COMMAND AND CONTROL POST |  | DN100 | 包括湿式报警阀本体,压力开关，水力警铃，过滤器，带锁阀门，延迟器，排水阀，警铃实验阀，上、下腔压力表，以及正确执行报警任务所必须的弯头、三通等管件、镀锌管等。Command and control post by levels, including safety valves, accessories, connections (hydraulic, electrical, fire, control etc) all materials and work needed to perfect and complete operation. Technical requirements, manufacturer and construction details according to specifications and drawings provided. | 合格qualified | CE | 台un | 2 | 参考消防水图纸，供应商予以深化，并提供湿式报警阀组的相关参数和安装图纸Reference fire water drawings to be deepened by suppliers, and provide the relevant detailed parameters and installation drawings
16 | 热能表 Thermal Meter | CEF — DN200 | DN250 | 规格 specification：DN250 型号Model：具体型号由厂家确定All models must be confirmed with the equipment supplier. 配备带脉冲能够控制器的水量流量计，包括脉冲输出Volume flow meter with impulse controller, including impulse exit; 用于热能的微处理器，内置显示屏并有M-BUS出口（至少有2个独立的出口），Microprocessors for thermal energy, with built-in display and equipped with M-BUS exit (with a minimum of 2 independent exits) 有电缆和温度探头（分配和返回），组合热电偶Cables and temperature probes (distribution and return), and built-up thermowells; | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：ZENNER / MINOL 安装在冷水指定回路上，法兰连接The thermal energy meters will be installed in the cooling circuits, as specified in the drawings 。Flange connection
17 | 热能表 Thermal Meter | CEQ — DN100 | DN125 | 规格 specification：DN125 型号Model：具体型号由厂家确定All models must be confirmed with the equipment supplier. 配备带脉冲能够控制器的水量流量计，包括脉冲输出Volume flow meter with impulse controller, including impulse exit; 用于热能的微处理器，内置显示屏并有M-BUS出口（至少有2个独立的出口），Microprocessors for thermal energy, with built-in display and equipped with M-BUS exit (with a minimum of 2 independent exits) 有电缆和温度探头（分配和返回），组合热电偶Cables and temperature probes (distribution and return), and built-up thermowells; | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：ZENNER / MINOL 安装在热水指定回路上，法兰连接The thermal energy meters will be installed in the heating circuits, as specified in the drawings 。Flange connection
18 | 保温罐INSULATED WATER TANKS | DIF |  | 容量Capacity ：2500 L ； 样式Model ：立式Vertical 按照CT要求配备压力计、温度表及必要的配件 Thermomet ers, manometers and all the accessories in compliance with the CT; 镁阳极防腐保护Anti-corrosion protection with a magnesium anode; 进行保温及机械防护Thermal insulation and mechanical protection; 立式固定和安装Fixations and supports for vertical installation; 排水阀门 Drain valves. | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： SANDOMETAL/ HOVAL 参看空调图纸，用于冷水管路Cold Water， 供应商予以深化并提供具体参数和安装尺寸It is used for Cold Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
19 | 保温罐INSULATED WATER TANKS | DAQ |  | 容量Capacity ：750 L ； 样式Model ：立式Vertical 按照CT要求配备压力计、温度表及必要的配件 Thermomet ers, manometers and all the accessories in compliance with the CT; 镁阳极防腐保护Anti-corrosion protection with a magnesium anode; 进行保温及机械防护Thermal insulation and mechanical protection; 立式固定和安装Fixations and supports for vertical installation; 排水阀门 Drain valves | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： SANDOMETAL/ HOVAL 参看空调图纸，用于热水管路HOT Water ，供应商予以深化并提供具体参数和安装尺寸It is used for Hot Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
20 | 机动膨胀水箱 MOTORIZED EXPANSION WATER Vessel | VE-F |  | 冷水容量Capacity ：750 L ； 电气性能Electric characteristics： 400V/3F/50Hz 功率power：1.1Kw 最大运行压力Maximum Operation Pressure：10bar 最高温度Maximum temperature：70℃ 样式Model ：立式Vertical 用于增压系统Compressor-controlled pressurization system; 配备自动断开阀、泄水阀、和截止阀Automatic cut-off valve, drain valve and sectioning valves; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：REFLEX / CALEFFI 参看空调图纸，用于冷水管路Cold Water， 供应商予以深化并提供具体参数和安装尺寸It is used for Cold Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
21 | 静态隔膜膨胀水箱 STATIC DIAPHRAGM EXPANSION WATER TANKS | VE-Q |  | 热水容量Capacity ：200 L ； 电气性能Electric characteristics： 400V/3F/50Hz 功率power：1.1Kw 最大运行压力Maximum Operation Pressure：6bar 最高温度Maximum temperature：70℃ 样式Model ：立式Vertical 隔膜式Membrane; 配备自动断开阀、泄水阀、和截止阀Automatic cut-off valve, drain valve and sectioning valves; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：REFLEX / CALEFFI 参看空调图纸，用于热水管路HOT Water ，供应商予以深化并提供具体参数和安装尺寸It is used for Hot Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
22 | 生活水换热器INSULATED WATER TANKS – DOMESTIC HOT WATER (DHW) | DAQS |  | 容量Capacity ：1000 L ； 电加热器 Electric Heat Exchanger [kW]：15 名义压力 Nominal Pressure [bar] ：8 最高温度Maximum Temperature [ºC] ：100 样式Model ：立式Vertical 不锈钢罐壁Stainless steel walls; 不锈钢内盘管 Stainless Steel coil; 按CT要求配压力表温度计Thermometers, manometers and all the accessories accordingly with the CT; 镁阳极防腐保护Anti-corrosion protection with a magnesium anode； 保温及外壁机械防护Thermal insulation and mechanical protection; 样式Model ：立式Vertical | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： SANDOMETAL / ZANI /VULCANO
23 | 电加热器 ELECTRIC HEATER |  |  | 容量CAPACITY：100升( Litros) 电气特性Electric characteristics： 230V/1F/50Hz 供应电热水器，包括安全阀，安全恒温温控器，阀门，膨胀箱，电气安全控制系统，卧式墙壁安装支架等。Supply and installation of high pressure electric water heaters, including safety valves, safety thermostat, valve, expansion vessel, electric safety control system, supports-structure, all connections and derivations (hydraulic, electrical, drainage etc.) and all materials and work needed to perfect operation. | 合格qualified | CE | 台un | 8
24 | 油烟集气罩 SMOKE EXHAUST - HOOD | HOOD-1 | 4000x1200x500 | 排气量Flow exhaust [m 3 /h] ：6750 带不锈钢送风口和排风口stainless steel plenums for exhaust and air supply 带油脂回收阀Valves for grease recovery; 带檐Visors; 带暗装照明灯 Embedded light; 带组装和安装配件Accessories for fixation and assembly; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR 厨房设备，304不锈钢制作Kitchen equipment,Stainless Steel AISI 304 18/10
25 | 厨房油脂分离器 grease separator chamber |  |  | 埋地式安装，Installation：buried underground 外形尺寸（参考）长x宽：Length x width（only for reference）： 1300*800 入口接管：Inlet：DN125 出口接管：Outlet：DN125 | 合格qualified |  | 台un | 1 | 参考品牌BRAND：TECHNEAU 厨房设备配套Kitchen equipment
26 | 油烟净化器ELECTROSTATIC FILTER MODULE | MFE–H | FEI7000 | 最大风量Air Flow Rate [m 3 /h] ：6750 最大压力损失Maximum Load Loss [Pa] ：100 | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR
27 | 变速油烟排气风机Variable Speed Plug HOTTE EXHAUST FAN | VEX-H |  | 风量Air Flow Rate [m 3 /h]： 6750 静压Static Pressure [Pa]：600 电机功率Motor Power [kW] ：3.0 声压级Sound Pressure Level dB (A) ：≤ 62 电机外置 Motor out of flow 三相电机Three-phase motor (400V/3F/50Hz) 防火等级Fire proof grade ：400°C/2H 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮和运行状态显示器Local stop push button and functioning state display; 带压差开关Differential air pressure switch; 变速控制器靠近油烟机安装 Speed variation controller to be installed near the Hotte | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
28 | 加压恒速轴流风机PRESSURIZATION Constant Speed Axial Fan | VPE |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：200 电机功率Motor Power [kW] ：0.55 防火等级Fire proof grade： 400°C/2H 三相电机Three-phase motor：400V/3F/50Hz 带长外壳Long casing 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 3 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
29 | 加压恒速轴流风机PRESSURIZATION Constant Speed Axial Fan | VPAC |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：200 电机功率Motor Power [kW] ：0.55 防火等级Fire proof grade： 400°C/2H 三相电机Three-phase motor：400V/3F/50Hz 带长外壳Long casing 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
30 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-0.3 |  | 风量Air Flow Rate [m 3 /h]： 1750 静压Static Pressure [Pa]：160 电机功率Motor Power [kW] ：0.32 单相电机Single-phase motor：230V/1F/50Hz 室内安装Indoor Installation 带吊装减震器Anti-Vibration suspensions; 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
31 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-C |  | 风量Air Flow Rate [m 3 /h]： 3420 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.75 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
32 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-B |  | 风量Air Flow Rate [m 3 /h]： 240 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.06 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
33 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-7.1 |  | 风量Air Flow Rate [m 3 /h]： 200 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.06 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
34 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-R |  | 风量Air Flow Rate [m 3 /h]： 2160 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.65 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
35 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-CZ |  | 风量Air Flow Rate [m 3 /h]： 660 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.45 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
36 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-0.1 |  | 风量Air Flow Rate [m 3 /h]： 345 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.08 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
37 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-0.2 |  | 风量Air Flow Rate [m 3 /h]： 1150 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.45 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
38 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-IS1 |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.75 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
39 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-IS2 |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：200 电机功率Motor Power [kW] ：0.75 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
40 | VRV壁挂式空调室内机 Wall Type UI–EVAPORATORS | UI–ATMF2 | MI-245 | 制冷量Cooling Capacity [kW] 4.5 风量Air Flow Rate [m 3 /h]：841 声压级Sound Pressure Level dB (A) ：≤ 38 电机功率Motor Power [kW] ：0.19 电气特性Electrical Characteristics ：230V/1F/50Hz 离心风扇带过滤器 Centrifugal Fan WITH Air Filters; 壁装控制器（或遥控器）,带电源线和温度传感器Local controller for wall installation (or infrared remote control) including power supply cables and temperature sensors ； 带安装支架Support structures | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的
41 | V.R.V系统室外机V.R.V. SYSTEM UE – CONDENSER | UE – ATMF2 | MV5 – X252W | 制冷量Cooling Capacity [kW]：25.2 电机功率Motor Power [kW] ：5.36 电气特性Electrical Characteristics ：400V/3F/50Hz 外形尺寸Dimensions(W × D × H) [mm] ：990x1635x790 重量Weight [Kg] ： 235 可变速上排风轴流风扇Axial fans with vertical air exhaust and variable speed 充装R410A 制冷剂 R410A refrigerant fluid charge (free of CFCs) 混凝土板上安装带减震支架 Concrete platform as foundation and anti-vibration supports 包括软件在内的每时和每周运行安排程序Central Scheduler for hourly and weekly programming of the system, including software 。 VRV系统选型要保证室内机之间的最大距离能达到30m，该距离由供应商确认 The VRV system was dimensioned to guarantee a maximum distance of 30m between the indoor units, distance which must be confirmed by the supplier | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 设备内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
42 | VRV壁挂式空调室内机 Wall Type UI–EVAPORATORS | UI–ATMF1 | MI – 28G | 制冷量Cooling Capacity [kW]2.8 风量Air Flow Rate [m 3 /h]：505 声压级Sound Pressure Level dB (A) ：≤ 31 电机功率Motor Power [kW] ：0.09 电气特性Electrical Characteristics ：230V/1F/50Hz 离心风扇带过滤器 Centrifugal Fan WITH Air Filters; 壁装控制器（或遥控器）,带电源线和温度传感器Local controller for wall installation (or infrared remote control) including power supply cables and temperature sensors ； 带安装支架Support structures | 合格qualified | CE | 台un | 6 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的
43 | V.R.V系统室外机V.R.V. SYSTEM UE – CONDENSER | UE – ATMF1 | MV5 – X252W | 制冷量Cooling Capacity [kW]：25.2 电机功率Motor Power [kW] ：5.36 电气特性Electrical Characteristics ：400V/3F/50Hz 外形尺寸Dimensions(W × D × H) [mm] ：990x1635x790 重量Weight [Kg] ： 235 可变速上排风轴流风扇Axial fans with vertical air exhaust and variable speed 充装R410A 制冷剂 R410A refrigerant fluid charge (free of CFCs) 混凝土板上安装带减震支架 Concrete platform as foundation and anti-vibration supports 包括软件在内的每时和每周运行安排程序Central Scheduler for hourly and weekly programming of the system, including software 。 VRV系统选型要保证室内机之间的最大距离能达到30m，该距离由供应商确认 The VRV system was dimensioned to guarantee a maximum distance of 30m between the indoor units, distance which must be confirmed by the supplier | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 设备内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
44 | 分体空调 Wall Type UI–EVAPORATORS | UI–ATE（ATT） UE–ATE(ATT) | MI–28G | 制冷量Cooling Capacity [kW]：2.5 制热量Heating Capacity [kW]：3.2 风量Air Flow Rate [m 3 /h]：336 连接管 Piping DN [mm]：L= 6.4 ；G= 9.5 电机功率Motor Power [kW] ：0.78 电气特性Electrical Characteristics ：230V/1F/50Hz 离心风扇带过滤器 Centrifugal Fan WITH Air Filters; 壁装控制器（或遥控器）,带电源线和温度传感器Local controller for wall installation (or infrared remote control) including power supply cables and temperature sensors ； 带安装支架Support structures 室外机侧排风轴流风扇Axial fans with sideways air xhaust; 充装R410A 制冷剂 R410A refrigerant fluid charge (free of CFCs) 带减震支架 anti-vibration supports 带就地维修按钮 Local stop push button; 图纸上显示的室内机与室外机的间距要由供应商来确认All the equipment models must be confirmed by the supplier for the distances between the indoor and outdoor units, as specified in the Drawings. | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 / DAIKIN 大金 设备内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
45 | 卡式风机盘管Cassette Fan Coil | VCC–1 | MKA | 制冷量Cooling Capacity [kW]：5.6 风量Air Flow Rate [m 3 /h]：1700 电机功率Motor Power [kW] ：0.17 声压级Sound Pressure Level [dB (A)]： ≤ 40 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch | 合格qualified | CE | 台un | 34 | 参考品牌BRAND： MIDEA美的 / AERMEC
46 | 卡式风机盘管Cassette Fan Coil | VCC–2 | MKA | 制冷量Cooling Capacity [kW]：7.0 风量Air Flow Rate [m 3 /h]：2170 电机功率Motor Power [kW] ：0.17 声压级Sound Pressure Level [dB (A)]： ≤ 40 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch | 合格qualified | CE | 台un | 164 | 参考品牌BRAND： MIDEA美的 / AERMEC
47 | 卡式风机盘管Cassette Fan Coil | VCC–3 | MKD | 制冷量Cooling Capacity [kW]：2.7 风量Air Flow Rate [m 3 /h]：850 电机功率Motor Power [kW] ：0.08 声压级Sound Pressure Level [dB (A)]： ≤ 40 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch | 合格qualified | CE | 台un | 12 | 参考品牌BRAND： MIDEA美的 / AERMEC
48 | 风管式风机盘管 Duct Fan Coil | VC-1 | TA | 制冷量Cooling Capacity [kW]：3.0 风量Air Flow Rate [m 3 /h]：1000 电机功率Motor Power [kW] ：0.37 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。
49 | 风管式风机盘管 Duct Fan Coil | VC-2 | TA | 制冷量Cooling Capacity [kW]：7.5 风量Air Flow Rate [m 3 /h]：1660 电机功率Motor Power [kW] ：0.66 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格qualified | CE | 台un | 11 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。
50 | 风管式风机盘管 Duct Fan Coil | VC-3 | TA | 制冷量Cooling Capacity [kW]：12.0 风量Air Flow Rate [m 3 /h]：3240 电机功率Motor Power [kW] ：1.28 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格qualified | CE | 台un | 7 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。
51 | 风管式风机盘管 Duct Fan Coil | VC-4 | TA | 制冷量Cooling Capacity [kW]：16.0 风量Air Flow Rate [m 3 /h]：3210 电机功率Motor Power [kW] ：1.26 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：150 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。
52 | 风管式风机盘管 Duct Fan Coil | VC-5 | TA | 制冷量Cooling Capacity [kW]：5.2 风量Air Flow Rate [m 3 /h]：1100 电机功率Motor Power [kW] ：0.4 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格qualified | CE | 台un | 4 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。
53 | 风管式风机盘管 Duct Fan Coil | VC-6 | TA | 制冷量Cooling Capacity [kW]：10.0 风量Air Flow Rate [m 3 /h]：1950 电机功率Motor Power [kW] ：0.51 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格qualified | CE | 台un | 3 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。
54 | 空气处理机组 AIR HANDLING UNITS | AHU–L1 |  | 制冷量Cooling Capacity [kW]：45.0 制热量Heating Capacity [kW]：35.0 送风量Air Flow Rate [m 3 /h]：9500 回风量 Return Air Flow Rate [m 3 /h]：9500 电机功率Motor Power [kW] ：3.45 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器F7 级F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带网络管理通信卡Network management system communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 带二氧化碳传感器 CO2 Sensor; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
55 | 空气处理机组 AIR HANDLING UNITS | AHU–L2 |  | 制冷量Cooling Capacity [kW]：35.0 制热量Heating Capacity [kW]：26.5 送风量Air Flow Rate [m 3 /h]：7000 回风量 REturn Air Flow Rate [m 3 /h]：7000 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器F7 级F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带网络管理通信卡Network management system communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 带二氧化碳传感器 CO2 Sensor; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
56 | 新风回风空气处理机组 Fresh AIR HANDLING UNITS | AHU–R |  | 制冷量Cooling Capacity [kW]：51.0 制热量Heating Capacity [kW]：15.0 送风量Air Flow Rate [m 3 /h]：5400 回风量REturn Air Flow Rate [m 3 /h]：2700 新风量 Fresh Air Flow Rate [m 3 /h]：2700 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 回风段不设调节阀Non return damper in the fresh air admission; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 带二氧化碳传感器 CO2 Sensor; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
57 | 全新风空气处理机组 (100% FRESH AIR)Fresh AIR HANDLING UNITS | FAHU–CZ |  | 制冷量Cooling Capacity [kW]：32.5 送风量Air Flow Rate [m 3 /h]：6615 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 新风入口段无调节阀Non return damper in the fresh air admission; 在风机的出口管设置消声段Acoustic attenuators on the discharge duct of the air supply fan ； | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
58 | 全新风空气处理机组 (100% FRESH AIR)Fresh AIR HANDLING UNITS | FAHU–0.1 |  | 制冷量Cooling Capacity [kW]：80.6 制热量Heating Capacity [kW]：14.5 送风量Air Flow Rate [m 3 /h]：5150 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 新风入口段无调节阀Non return damper in the fresh air admission; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
59 | 全新风空气处理机组 (100% FRESH AIR)Fresh AIR HANDLING UNITS | FAHU–C |  | 制冷量Cooling Capacity [kW]：64.3 制热量Heating Capacity [kW]：11.2 送风量Air Flow Rate [m 3 /h]：4000 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 新风入口段无调节阀Non return damper in the fresh air admission; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
60 | 热回收式全新风空气处理机组 (100% FRESH AIR)FRESH AIR HANDLING UNITS WITH ENERGY RECOVERY | FAHU–A |  | 制冷量Cooling Capacity [kW]：113.5 ； 制热量Heating Capacity [kW]：27.6 热回收冷量 Recovery Cooling Capacity [kW] ：24.0 热回收热量 Recovery Heating Capacity [kW] ：44.0 送风量Sup.Air Flow Rate [m 3 /h]：9625 ； 排风量Exh.Air Flow Rate [m 3 /h]：5335 送风电机功率Motor Power Sup. [kW] ：5.7 ； 排风电机功率Motor Power Exh. [kW] ：5.7 热回收电机功率Motor Power Rec. [kW]：0.25 ； 静压 Static Pressure [Pa]：300 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 送风机和排风机样式：Plug Fan ，Plug Fan for air supply and air rejection 带变速控制器Speed Variation Controller ； 送风段过滤器G4+F7 级，Sup.G4+F7 class filters ； 热回收段过滤器F7 级，Rec.G4+F7 class filters ； 吸湿性轮式热交换器Hygroscopic Wheel type heat exchanger 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 混凝土板为基础，配备减振器Concrete platform as foundation and anti-vibration supports; 在送风机的出口管和排风机入口管设置消声段Acoustic attenuators on the discharge duct of the air supply fan and on the aspiration duct of the extraction fan; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
61 | 热回收式全新风空气处理机组 (100% FRESH AIR)FRESH AIR HANDLING UNITS WITH ENERGY RECOVERY | FAHU–B |  | 制冷量Cooling Capacity [kW]：113.5 ； 制热量Heating Capacity [kW]：27.6 热回收冷量 Recovery Cooling Capacity [kW] ：26.0 热回收热量 Recovery Heating Capacity [kW] ：46.0 送风量Sup.Air Flow Rate [m 3 /h]：9625 ； 排风量Exh.Air Flow Rate [m 3 /h]：5430 送风电机功率Motor Power Sup. [kW] ：5.7 ； 排风电机功率Motor Power Exh. [kW] ：5.7 热回收电机功率Motor Power Rec. [kW]：0.25 ； 静压 Static Pressure [Pa]：300 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 送风机和排风机样式：Plug Fan ，Plug Fan for air supply and air rejection 带变速控制器Speed Variation Controller ； 送风段过滤器G4+F7 级，Sup.G4+F7 class filters ； 热回收段过滤器F7 级，Rec.G4+F7 class filters ； 吸湿性轮式热交换器Hygroscopic Wheel type heat exchanger 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
62 | 带热回收的螺杆式制冷机组THERMAL PRODUCTION UNITS –Screw Type CHILLERS (COOLING ONLY WITH HEAT RECOVERY) | CH – 1,2 | 30XA 1002-A | 制冷量Cooling Capacity [kW]：976； 回收量 Recovery Capacity [kW] ：313 电机功率Motor Power[kW] ：314.2 电气性能 Electric Characteristics ：400V/3F/50Hz 10米噪声等级Noise Level [dB (A)] – 10m： ≤ 68 外形尺寸Dimensions (LxWxH) [mm]： 9574x2253x2297 重量Weight [Kg]：8870 工作媒介 Working Fluid ：R134a 运行温度 Operating temperatures: 冷水Cold Water – 7ºC/12ºC ； 热水回收Hot Water (Recovery) – 45ºC/40ºC； 设备配置 The units will be equipped and supplied with: 螺杆式压缩机Screw type compressors; 部分回收式换热器 Heat exchanger for partial heat recovery; 风冷式冷凝器Air cooled condensers; 竖排式轴流风扇 Axial fans with vertical discharge; 有微处理控制器的电气柜，能与楼宇自控系统BMS通信Electric and command switchboard with microprocessor control system for communication with the Building Management System (BMS); 低噪声装备Kit Low Noise; | 合格qualified |  | 台un | 2 | 参考品牌BRAND:开利CARRIER/特灵RANE/RCAT 设备为气水式冷水制备系统，带部分热回收式交换器The units will be of the air-water type for cold water production and equipped with heat exchanger for partial heat recovery. 设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. 室外设计条件：Outdoor design conditions: 夏季 Summer – 35°C – HR: 85% 冬季Winter – 19°C – HR: 75%

## 空调招标 (hidden)
序号 | 名称 | 图例 | 规格 | 主要技术参数 | 质量要求 | 认证 | 单位 | 工程量 | 备注说明 | 计划进场时间 | 计划国内港口发货时间 | 预计生产周期（日历天） | 计划招标完成时间 | 品牌 | 规格型号 | 主要技术参数 | 单价 | 总价 | 备注说明
3 | 卡式风机盘管Cassette Fan Coil | VCC–1 | MKA | 制冷量Cooling Capacity [kW]：5.6 风量Air Flow Rate [m 3 /h]：1700 电机功率Motor Power [kW] ：0.17 声压级Sound Pressure Level [dB (A)]： ≤ 40 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch | 合格 | CE | 台 | 34 | 参考品牌BRAND： MIDEA美的 / AERMEC | #VALUE! | #VALUE! | 30 | #VALUE!
4 | 卡式风机盘管Cassette Fan Coil | VCC–2 | MKA | 制冷量Cooling Capacity [kW]：7.0 风量Air Flow Rate [m 3 /h]：2170 电机功率Motor Power [kW] ：0.17 声压级Sound Pressure Level [dB (A)]： ≤ 40 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch | 合格 | CE | 台 | 164 | 参考品牌BRAND： MIDEA美的 / AERMEC | #VALUE! | #VALUE! | 30 | #VALUE!
5 | 卡式风机盘管Cassette Fan Coil | VCC–3 | MKD | 制冷量Cooling Capacity [kW]：2.7 风量Air Flow Rate [m 3 /h]：850 电机功率Motor Power [kW] ：0.08 声压级Sound Pressure Level [dB (A)]： ≤ 40 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch | 合格 | CE | 台 | 12 | 参考品牌BRAND： MIDEA美的 / AERMEC | #VALUE! | #VALUE! | 30 | #VALUE!
6 | 风管式风机盘管 Duct Fan Coil | VC-1 | TA | 制冷量Cooling Capacity [kW]：3.0 风量Air Flow Rate [m 3 /h]：1000 电机功率Motor Power [kW] ：0.37 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格 | CE | 台 | 2 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。 | #VALUE! | #VALUE! | 30 | #VALUE!
7 | 风管式风机盘管 Duct Fan Coil | VC-2 | TA | 制冷量Cooling Capacity [kW]：7.5 风量Air Flow Rate [m 3 /h]：1660 电机功率Motor Power [kW] ：0.66 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格 | CE | 台 | 11 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。 | #VALUE! | #VALUE! | 30 | #VALUE!
8 | 风管式风机盘管 Duct Fan Coil | VC-3 | TA | 制冷量Cooling Capacity [kW]：12.0 风量Air Flow Rate [m 3 /h]：3240 电机功率Motor Power [kW] ：1.28 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格 | CE | 台 | 7 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。 | #VALUE! | #VALUE! | 30 | #VALUE!
9 | 风管式风机盘管 Duct Fan Coil | VC-4 | TA | 制冷量Cooling Capacity [kW]：16.0 风量Air Flow Rate [m 3 /h]：3210 电机功率Motor Power [kW] ：1.26 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：150 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格 | CE | 台 | 1 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。 | #VALUE! | #VALUE! | 30 | #VALUE!
10 | 风管式风机盘管 Duct Fan Coil | VC-5 | TA | 制冷量Cooling Capacity [kW]：5.2 风量Air Flow Rate [m 3 /h]：1100 电机功率Motor Power [kW] ：0.4 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格 | CE | 台 | 4 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。 | #VALUE! | #VALUE! | 30 | #VALUE!
11 | 风管式风机盘管 Duct Fan Coil | VC-6 | TA | 制冷量Cooling Capacity [kW]：10.0 风量Air Flow Rate [m 3 /h]：1950 电机功率Motor Power [kW] ：0.51 声压级Sound Pressure Level [dB (A)]： ≤ 40 静压 Static Pressure [Pa]：120 电气特性Electrical Characteristics ：230V/1F/50Hz 就地控制器包括恒温器、三速开关Local controller including an ambient thermostat, fan speed control, with a minimum of three fan speeds, and an on-off switch 四级过滤器G4 class filters 风机名义运行条件中风速和静压有风管系统决定The nominal operating conditions for the fan speed and the static pressure will be confirmed depending on the duct system. 盘管风机名义运行条件按照风扇中速决定The nominal operating conditions for the fan coils relate to the fan's intermediate speeds. 风机静压要考虑施工现场风管的实际情况The static pressure will be confirmed considering the real ductwork, at the construction site。 | 合格 | CE | 台 | 3 | 参考品牌BRAND： MIDEA美的 / AERMEC 严格控制设备噪声等级，或采取相应技术措施，满足噪声要求。 | #VALUE! | #VALUE! | 30 | #VALUE!
12 | 空气处理机组 AIR HANDLING UNITS | AHU–L1 |  | 制冷量Cooling Capacity [kW]：45.0 制热量Heating Capacity [kW]：35.0 送风量Air Flow Rate [m 3 /h]：9500 回风量 Return Air Flow Rate [m 3 /h]：9500 电机功率Motor Power [kW] ：3.45 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器F7 级F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带网络管理通信卡Network management system communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 带二氧化碳传感器 CO2 Sensor; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 60 | #VALUE!
13 | 空气处理机组 AIR HANDLING UNITS | AHU–L2 |  | 制冷量Cooling Capacity [kW]：35.0 制热量Heating Capacity [kW]：26.5 送风量Air Flow Rate [m 3 /h]：7000 回风量 REturn Air Flow Rate [m 3 /h]：7000 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器F7 级F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带网络管理通信卡Network management system communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 带二氧化碳传感器 CO2 Sensor; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 60 | #VALUE!
14 | 新风回风空气处理机组 Fresh AIR HANDLING UNITS | AHU–R |  | 制冷量Cooling Capacity [kW]：51.0 制热量Heating Capacity [kW]：15.0 送风量Air Flow Rate [m 3 /h]：5400 回风量REturn Air Flow Rate [m 3 /h]：2700 新风量 Fresh Air Flow Rate [m 3 /h]：2700 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 回风段不设调节阀Non return damper in the fresh air admission; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 带二氧化碳传感器 CO2 Sensor; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 60 | #VALUE!
15 | 全新风空气处理机组 (100% FRESH AIR)Fresh AIR HANDLING UNITS | FAHU–CZ |  | 制冷量Cooling Capacity [kW]：32.5 送风量Air Flow Rate [m 3 /h]：6615 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 新风入口段无调节阀Non return damper in the fresh air admission; 在风机的出口管设置消声段Acoustic attenuators on the discharge duct of the air supply fan ； | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 60 | #VALUE!
16 | 全新风空气处理机组 (100% FRESH AIR)Fresh AIR HANDLING UNITS | FAHU–0.1 |  | 制冷量Cooling Capacity [kW]：80.6 制热量Heating Capacity [kW]：14.5 送风量Air Flow Rate [m 3 /h]：5150 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 新风入口段无调节阀Non return damper in the fresh air admission; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 60 | #VALUE!
17 | 全新风空气处理机组 (100% FRESH AIR)Fresh AIR HANDLING UNITS | FAHU–C |  | 制冷量Cooling Capacity [kW]：64.3 制热量Heating Capacity [kW]：11.2 送风量Air Flow Rate [m 3 /h]：4000 电机功率Motor Power [kW] ：2.5 静压 Static Pressure [Pa]：250 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 风机样式Plug Fan ； 带变速控制器Speed Variation Controller ； 过滤器G4+F7 级，G4+F7 class filters ； 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 采用减振器及金属结构吊装在天花板上Metallic structure for equipment fixation on the ceiling and anti-vibration； 新风入口段无调节阀Non return damper in the fresh air admission; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 60 | #VALUE!
18 | 带热回收的螺杆式制冷机组THERMAL PRODUCTION UNITS –Screw Type CHILLERS (COOLING ONLY WITH HEAT RECOVERY) | CH – 1,2 | 30XA 1002-A | 制冷量Cooling Capacity [kW]：976； 回收量 Recovery Capacity [kW] ：313 电机功率Motor Power[kW] ：314.2 电气性能 Electric Characteristics ：400V/3F/50Hz 10米噪声等级Noise Level [dB (A)] – 10m： ≤ 68 外形尺寸Dimensions (LxWxH) [mm]： 9574x2253x2297 重量Weight [Kg]：8870 工作媒介 Working Fluid ：R134a 运行温度 Operating temperatures: 冷水Cold Water – 7ºC/12ºC ； 热水回收Hot Water (Recovery) – 45ºC/40ºC； 设备配置 The units will be equipped and supplied with: 螺杆式压缩机Screw type compressors; 部分回收式换热器 Heat exchanger for partial heat recovery; 风冷式冷凝器Air cooled condensers; 竖排式轴流风扇 Axial fans with vertical discharge; 有微处理控制器的电气柜，能与楼宇自控系统BMS通信Electric and command switchboard with microprocessor control system for communication with the Building Management System (BMS); 低噪声装备Kit Low Noise; |  |  | 台 | 2 | 参考品牌BRAND:开利CARRIER/特灵RANE/RCAT 设备为气水式冷水制备系统，带部分热回收式交换器The units will be of the air-water type for cold water production and equipped with heat exchanger for partial heat recovery. 设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. 室外设计条件：Outdoor design conditions: 夏季 Summer – 35°C – HR: 85% 冬季Winter – 19°C – HR: 75% | #VALUE! | #VALUE! | 120 | #VALUE!
30 | 热回收式全新风空气处理机组 (100% FRESH AIR)FRESH AIR HANDLING UNITS WITH ENERGY RECOVERY | FAHU–A |  | 制冷量Cooling Capacity [kW]：113.5 ； 制热量Heating Capacity [kW]：27.6 热回收冷量 Recovery Cooling Capacity [kW] ：24.0 热回收热量 Recovery Heating Capacity [kW] ：44.0 送风量Sup.Air Flow Rate [m 3 /h]：9625 ； 排风量Exh.Air Flow Rate [m 3 /h]：5335 送风电机功率Motor Power Sup. [kW] ：5.7 ； 排风电机功率Motor Power Exh. [kW] ：5.7 热回收电机功率Motor Power Rec. [kW]：0.25 ； 静压 Static Pressure [Pa]：300 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 送风机和排风机样式：Plug Fan ，Plug Fan for air supply and air rejection 带变速控制器Speed Variation Controller ； 送风段过滤器G4+F7 级，Sup.G4+F7 class filters ； 热回收段过滤器F7 级，Rec.G4+F7 class filters ； 吸湿性轮式热交换器Hygroscopic Wheel type heat exchanger 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; 混凝土板为基础，配备减振器Concrete platform as foundation and anti-vibration supports; 在送风机的出口管和排风机入口管设置消声段Acoustic attenuators on the discharge duct of the air supply fan and on the aspiration duct of the extraction fan; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 90 | #VALUE!
31 | 热回收式全新风空气处理机组 (100% FRESH AIR)FRESH AIR HANDLING UNITS WITH ENERGY RECOVERY | FAHU–B |  | 制冷量Cooling Capacity [kW]：113.5 ； 制热量Heating Capacity [kW]：27.6 热回收冷量 Recovery Cooling Capacity [kW] ：26.0 热回收热量 Recovery Heating Capacity [kW] ：46.0 送风量Sup.Air Flow Rate [m 3 /h]：9625 ； 排风量Exh.Air Flow Rate [m 3 /h]：5430 送风电机功率Motor Power Sup. [kW] ：5.7 ； 排风电机功率Motor Power Exh. [kW] ：5.7 热回收电机功率Motor Power Rec. [kW]：0.25 ； 静压 Static Pressure [Pa]：300 电气特性Electrical Characteristics ：Three-phase motor (400V/3F/50Hz) 送风机和排风机样式：Plug Fan ，Plug Fan for air supply and air rejection 带变速控制器Speed Variation Controller ； 送风段过滤器G4+F7 级，Sup.G4+F7 class filters ； 热回收段过滤器F7 级，Rec.G4+F7 class filters ； 吸湿性轮式热交换器Hygroscopic Wheel type heat exchanger 在通风管段及过滤器段设压差开关及足量的温湿度传感器Differential air pressure switch (in the filtering and ventilation sections), and probes of temperature and humidity, adequate for a proper performance control; 在通风段布置就地维修停机按钮 Local stop push button in the ventilation sections ； 凝结水盘为不锈钢AISI 316 Droplet separator with condensates drain pan in stainless steel AISI 316; 在通风段设置机内照明Internal lighting in the ventilation modules ； 保温外壳带维修门和检视窗 Insulated casing, maintenance access doors and inspection windows 带楼宇自控管理通信卡 Building Management System (BMS) communication card; | 合格 | CE | 台 | 1 | 参考品牌BRAND：FRANCE AIR / MIDEA美的 / SANDOMETAL 表中各组成模块的特性及施工现场的实际压头必须由供应商予以确认 All models must be confirmed, by the equipment suppliers, for the characteristics contained in this map and for the real head pressure at the construction site. AHUs设备内外组成元件必须防腐处理，以适应近海环境The AHUs must include an anticorrosion treatment, for their internal and external components, specific for near sea environments. | #VALUE! | #VALUE! | 90 | #VALUE!
58 | VRV壁挂式空调室内机 Wall Type UI–EVAPORATORS | UI–ATMF2 | MI-245 | 制冷量Cooling Capacity [kW] 4.5 风量Air Flow Rate [m 3 /h]：841 声压级Sound Pressure Level dB (A) ：≤ 38 电机功率Motor Power [kW] ：0.19 电气特性Electrical Characteristics ：230V/1F/50Hz 离心风扇带过滤器 Centrifugal Fan WITH Air Filters; 壁装控制器（或遥控器）,带电源线和温度传感器Local controller for wall installation (or infrared remote control) including power supply cables and temperature sensors ； 带安装支架Support structures | 合格 | CE | 台 | 2 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 | #VALUE! | #VALUE! | 60 | #VALUE!
59 | V.R.V系统室外机V.R.V. SYSTEM UE – CONDENSER | UE – ATMF2 | MV5 – X252W | 制冷量Cooling Capacity [kW]：25.2 电机功率Motor Power [kW] ：5.36 电气特性Electrical Characteristics ：400V/3F/50Hz 外形尺寸Dimensions(W × D × H) [mm] ：990x1635x790 重量Weight [Kg] ： 235 可变速上排风轴流风扇Axial fans with vertical air exhaust and variable speed 充装R410A 制冷剂 R410A refrigerant fluid charge (free of CFCs) 混凝土板上安装带减震支架 Concrete platform as foundation and anti-vibration supports 包括软件在内的每时和每周运行安排程序Central Scheduler for hourly and weekly programming of the system, including software 。 VRV系统选型要保证室内机之间的最大距离能达到30m，该距离由供应商确认 The VRV system was dimensioned to guarantee a maximum distance of 30m between the indoor units, distance which must be confirmed by the supplier | 合格 | CE | 台 | 1 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 设备内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments | #VALUE! | #VALUE! | 60 | #VALUE!
60 | VRV壁挂式空调室内机 Wall Type UI–EVAPORATORS | UI–ATMF1 | MI – 28G | 制冷量Cooling Capacity [kW]2.8 风量Air Flow Rate [m 3 /h]：505 声压级Sound Pressure Level dB (A) ：≤ 31 电机功率Motor Power [kW] ：0.09 电气特性Electrical Characteristics ：230V/1F/50Hz 离心风扇带过滤器 Centrifugal Fan WITH Air Filters; 壁装控制器（或遥控器）,带电源线和温度传感器Local controller for wall installation (or infrared remote control) including power supply cables and temperature sensors ； 带安装支架Support structures | 合格 | CE | 台 | 6 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 | #VALUE! | #VALUE! | 60 | #VALUE!
61 | V.R.V系统室外机V.R.V. SYSTEM UE – CONDENSER | UE – ATMF1 | MV5 – X252W | 制冷量Cooling Capacity [kW]：25.2 电机功率Motor Power [kW] ：5.36 电气特性Electrical Characteristics ：400V/3F/50Hz 外形尺寸Dimensions(W × D × H) [mm] ：990x1635x790 重量Weight [Kg] ： 235 可变速上排风轴流风扇Axial fans with vertical air exhaust and variable speed 充装R410A 制冷剂 R410A refrigerant fluid charge (free of CFCs) 混凝土板上安装带减震支架 Concrete platform as foundation and anti-vibration supports 包括软件在内的每时和每周运行安排程序Central Scheduler for hourly and weekly programming of the system, including software 。 VRV系统选型要保证室内机之间的最大距离能达到30m，该距离由供应商确认 The VRV system was dimensioned to guarantee a maximum distance of 30m between the indoor units, distance which must be confirmed by the supplier | 合格 | CE | 台 | 1 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 设备内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments | #VALUE! | #VALUE! | 60 | #VALUE!
62 | 分体空调 Wall Type UI–EVAPORATORS | UI–ATE（ATT） UE–ATE(ATT) | MI–28G | 制冷量Cooling Capacity [kW]：2.5 制热量Heating Capacity [kW]：3.2 风量Air Flow Rate [m 3 /h]：336 连接管 Piping DN [mm]：L= 6.4 ；G= 9.5 电机功率Motor Power [kW] ：0.78 电气特性Electrical Characteristics ：230V/1F/50Hz 离心风扇带过滤器 Centrifugal Fan WITH Air Filters; 壁装控制器（或遥控器）,带电源线和温度传感器Local controller for wall installation (or infrared remote control) including power supply cables and temperature sensors ； 带安装支架Support structures 室外机侧排风轴流风扇Axial fans with sideways air xhaust; 充装R410A 制冷剂 R410A refrigerant fluid charge (free of CFCs) 带减震支架 anti-vibration supports 带就地维修按钮 Local stop push button; 图纸上显示的室内机与室外机的间距要由供应商来确认All the equipment models must be confirmed by the supplier for the distances between the indoor and outdoor units, as specified in the Drawings. | 合格 | CE | 台 | 2 | 参考品牌BRAND： MITSUBISHI三菱 / MIDEA美的 / DAIKIN 大金 设备内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments | #VALUE! | #VALUE! | 60 | #VALUE!
总价
报价含17%增值税、包装费（出口包装）、运输费（国内指定港口）、商检费（如需商检）

## pump水泵招标 (hidden)
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
8 | 给水泵集成 SUPPLY WATER PUMPING SYSTEM |  |  | 流量Q=7 l/s,（同时系数 = 20%）， 扬程HM= 63.80 m, 几何压头：38.8m ，最小压力：100 kPa ，持续负载损失：15m，功率：2 x 4 kW + 4 kW 泵组成：2组+ 1个备用组，及两用一备。包括控制配电柜及具有所有电气连接，报警系统，稳压液气罐，转换阀、不锈钢管道和抽吸和输送歧管，不锈钢集水器，金属支架， 减振基础 。所用水泵为变速泵。 Supply pumping Central flow Q=7 l/s,（Simultaneity coefficient = 20% ），HM= 63,80 m, Geometric Head ：38,80 m，Minimum Pressure ： 100KPa，Continuous load loss ：15 m。power：2 x 4 kW + 4 kW made up 2 groups + 1 reserve group, including command and control switchboard of groups with all the electrical connections, alarm system, hydropneumatic tank, switching valves and stainless steel conections, disassembly joints, sectioning valves, piping and suction and delivery manifolds in stainless steel. metallic bench, antivibration supports。 All pumps are variable speed 。 | 合格qualified | CE | 台un | 1 | 参考型号/厂商Model/producer ：HU VP 3/1010 / KSB 参考给水图纸，供应商予以深化，并提供不锈钢给水泵集成的相关参数和安装图纸Reference to the water supply drawings to be deepened by suppliers ，and provide supply water stainless steel pumping integration related parameters and installation drawings
9 | 潜污泵submersible pump | PBD |  | 流量Q =6 l/s (同时系数Simultaneity coefficient = 26%) 扬程Hm =8 MCA, 几何压头 Geometric Head： 6 m 电机功率Motor Power[kW] ：1.8KW+1.8KW 最小压力Minimum Pressure ： 10 kPa 连续负载损失Continuous load loss： 1 m 组成：一用一备。 配置潜污泵液位控制配电箱，液位开关及连接防水线缆等必备配件composed by 1 submersible group + 1 submersible group reserve, installed in pumping well including auxiliary equipment (level switch, sectioning valves and discharge pipes, retention, screws, suction filter and other necessary accessories, electrical installations, Electrical switchboard, all connections included and all work and materials necessary for correct installation, everything according technical specifications. | 合格qualified | CE | 台un | 2 | 参考型号/厂商Model/producer ：Amarex NF 65-220/024 ULG – 195 / KSB 参考排污水图纸，供应商予以深化，配套供应配电箱、液位开关及连接用的防水电缆等必备附件Reference draining water drawings to be deepened by suppliers ,and provide matching distribution box, level switches and waterproof cables and other necessary accessories
10 | 二次加热回路变速管道泵SECONDARY HEATING CIRCUIT Variable Speed IN - LINE Pumps | BDQ |  | 水流量Water Flow [m 3 /h]：36 扬程 Head [m.w.c.]：20 电机功率Motor Power[kW] ：3.5 转速Speed ：可变速Variable 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 4 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 三用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
11 | 二次制冷回路变速管道泵SECUNDARY COOLING CIRCUIT Variable Speed IN - LINE Pumps | BDF |  | 水流量Water Flow [m 3 /h]：199.8 扬程 Head [m.w.c.]：20 电机功率Motor Power[kW] ：15 转速Speed ：可变速Variable 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 3 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 两用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
12 | 一次加热回路定速管道泵PRIMARY HEATING CIRCUIT Constant Speed IN - LINE Pumps | BPQ |  | 水流量Water Flow [m 3 /h]：54 扬程 Head [m.w.c.]：10 电机功率Motor Power[kW] ：2.5 转速Speed ：定速Constant 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 3 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 两用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
13 | 一次制冷回路定速管道泵PRIMARY COOLING CIRCUIT Constant Speed IN - LINE Pumps | BPF |  | 水流量Water Flow [m 3 /h]：168.4 扬程 Head [m.w.c.]：10 电机功率Motor Power[kW] ：7.5 转速Speed ：定速Constant 电气性能 Electric Characteristics ：400V/3F/50Hz 温度范围 Temperature Regimen [°C] ： ≤ 90 配备压差开关Differential water pressure switches; 为卧式泵配备减振支架 Equiped Anti-vibration supports for the horizontal pump installation in proper foundations; 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 3 | 参考品牌BRAND：格兰富Grundfos/WILO威乐 两用一备，水泵安装在机房内，所有型号（变速泵和定速泵）要确认安装中的实际压力损失 The Pumps will be installed in a technical room, and all models must be confirmed for the real pressure losses verified in the installation, for each system (variable or constant flow)设备内外组成元件必须防腐处理，以适应近海环境The equipment must include an anticorrosion treatment, for their internal and external components, specific for near sea environments.
14 | 消防水泵集成 Fire pump integration |  |  | 设计流量：Q=34 L/s ( 122,40 m³/h )，扬程 HM=85m， 水泵功率45 kW + 45 kW + 2.1kw 泵组成： 两台泵+一台稳压泵。 主泵符合标准EN 12845,单级卧式离心泵，主泵一用一备，轴向吸水，径向压缩符合标准 DIN24255， not self-priming。可调叶轮机械密封，自润滑轴承，三相异步电动机，风扇冷却，满足DIN和IEC 标准。 辅助稳压泵多级立式离心屏蔽泵，铸铁联轴器，，可调叶轮机械密封，自润滑轴承，三相异步电动机，风扇冷却，满足DIN和IEC 标准。参考型号。 消防电气控制箱QEP-1EAC ，金属材质，防护等级IP54，RAL3020 红色,接收并能发出24V电的信号指令，能自动启泵，手动停泵，具有消防泵远程启动/停止的接口端子并做好标记，其它标准组件，满足 EN 12845要求和葡萄牙规范。提供安装及操作说明书，泵站组件图，水泵性能曲线图，工厂调试合格证书。 具备消防电气集成控制箱，电气报警装置及各泵的连接线、控制线，电接点压力表，安全阀，气液膜式稳压罐，泵开关，泵口软连接，不锈钢连接管、带盲板法兰的分水器，甘油浴压力表，止回阀，薄膜流量计，正确执行消防水灭火任务所必须的内部连接件以及铸铁GG25.减振底板基础。Supply pumping Central FLOW Q=34 L/s = 122,40 m³/h to the distribution network of fire network system, made up of 2 pump groups + 1 auxiliar pump, model EDS EC 120-85 JEE / KSB , including command and control switchboard of groups with all the electrical connections, alarm system, hydropneumatic tank, switching valves and stainless steel conections, disassembly joints, piping and suction and delivery manifolds in stainless steell. Float slab, connections (hydraulic, electrical, control, fire etc) and derivation and all materials and work needed to perfect operation as technical specifications. Technical requirements, manufacturer and other construction detail according to specifications and drawings provided. | 合格qualified | CE | 台un | 1 | 参考型号/厂商Model/producer: EDS EC 120-85 JEE / KSB 参考消防水图纸，供应商予以深化，并提供相关泵组详细参数和安装图纸Reference fire water drawings to be deepened by suppliers, and provide the relevant pump group detailed parameters and installation drawings+A8E8A7:J8A7:J8A6:J8E8A7:J8B6:J8B5:J8

## water treatment水处理设备招标
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
1 | 自动软化水处理器AUTOMATIC DECALCIFIER |  |  | 型号MODEL：ECB 最大流量Maximum Flow ：1500l/h 电气性能Electric characteristics ：220V/50Hz 最大运行压力Maximum Operation Pressure： 7Kg/cm 2 最小运行压力Minimum Operation Pressure： 2Kg/cm 2 容量Capacity： 80 L | 合格qualified | CE | 台un | 1 | 参考品牌Reference Brand or Equivalent：ERIE / ENKROTT 空调软化水处理成套设备，参看空调图纸， 供应商予以深化并提供具体参数和安装尺寸 demineralized water treatment equipment for air conditioning system， see air-conditioning drawings to be deepen by suppliers ,and provide specific parameters and installation dimensions
2 | 计量表 DOSING AREA |  |  | 型号MODEL： DMREVRO 流量Flow Rate： 2 a 11 l/h 电气性能Electric characteristics： 380V/50Hz 最大运行压力Maximum Operation Pressure ：7.5Kg/cm 2 脉动频率Pulsation Frequence：120 pm | 合格qualified | CE | 台un | 1 | 参考品牌Reference Brand or Equivalent：ERIE / ENKROTT 空调软化水处理成套设备，参看空调图纸， 供应商予以深化并提供具体参数和安装尺寸 demineralized water treatment equipment for air conditioning system， see air-conditioning drawings to be deepen by suppliers ,and provide specific parameters and installation dimensions
3 | 计量泵 DOSING PUMP |  |  | 型号MODEL： DMREVRO 流量Flow Rate ：2 a 11 l/h 电气性能Electric characteristics： 380V/50Hz 最大运行压力Maximum Operation Pressure： 7.5Kg/cm 2 脉动频率Pulsation Frequence：120 pm ~ 容量Capacity： 110 L | 合格qualified | CE | 台un | 1 | 参考品牌Reference Brand or Equivalent：ERIE / ENKROTT 空调软化水处理成套设备，参看空调图纸， 供应商予以深化并提供具体参数和安装尺寸 demineralized water treatment equipment for air conditioning system， see air-conditioning drawings to be deepen by suppliers ,and provide specific parameters and installation dimensions
4 | 静态空气及污垢分离器Static TYPE AIR AND DIRT SEPARATORS | SAP–F | DN250 | 最大压力Max Pressure [bar]： 10 水流量Water Flow Rate [m3/h] ：1684 | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：SPIROVENT / CALEFFI 用于制冷回水管路Cooling Circuit (Return)， 供应商予以深化并提供具体参数和安装尺寸 Ror Cooling Circuit (Return), Supplier Deepens the drawings and Provide Specific Parameters and Mounting Dimensions
5 | 静态空气及污垢分离器Static TYPE AIR AND DIRT SEPARATORS | SAP–Q | DN125 | 最大压力Max Pressure [bar]： 10 水流量Water Flow Rate [m3/h] ：540 | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：SPIROVENT / CALEFFI 参看空调图纸，用于制冷回水管路Cooling Circuit (Return) ，供应商予以深化并提供具体参数和安装尺寸Ror Cooling Circuit (Return), Supplier Deepens the drawings and Provide Specific Parameters and Mounting Dimensions
6 | 氯化水处理器集成CHLORINE DOSING TREATMENT OF WATER |  |  | 水处理设备，有完整的氯/ pH值控制器，具有流量检测计。有消毒剂存储罐及计量泵，配电气控制箱和减振基础。配电箱预留楼宇自控BMS的通信接口Water treatment equipment,Complete chlorine/pH controller with flow detector.Complete chlorine/pH controller with flow detector.Dosing pump (disinfectant).Deposits tanks (disinfectant).Electrical-control panel. In coodination with BMS installations needs Electrical and control installation included。 | 合格qualified | CE | 台un | 1 | 参考给水图纸，供应商予以深化，并提供氯化水处理器集成相关参数和安装图纸Reference to the water supply drawings, to be deepened by suppliers， and provide chlorinated water processor integration related parameters and installation drawings
7 | 氯化水循环泵集成WATER RECIRCULATION PUMPING SYSTEM |  |  | 流量Q=4 l/s,扬程 HM= 12.00 m，几何压头：4m ，最小压力：50 kPa ，持续负载损失：3m，功率：1.1 kW + 1.1kW 泵组成：一用一备 。包括控制配电柜及具有所有电气连接，报警系统，稳压液气罐，转换阀、不锈钢管道和抽吸和输送歧管，不锈钢集水器，金属支架， 减振基础 。所用水泵为变速泵。 Supply pumping Central flow Q=4 l/s,，HM=12 m, Geometric Head ：4 m，Minimum Pressure ： 50KPa，Continuous load loss ：3m。power：1.1 kW+1.1kW made up 1 groups + 1 reserve group, including command and control switchboard of groups with all the electrical connections, alarm system, hydropneumatic tank, switching valves and stainless steel conections, disassembly joints, sectioning valves, piping and suction and delivery manifolds in stainless steell. metallic bench, antivibration supports。 All pumps are variable speed | 合格qualified | CE | 台un | 1 | 参考型号/厂商Model/producer ：ETL 32-32-160 GB / KSB 参考给水图纸，供应商予以深化，并提供氯化水循环泵集成相关参数和安装图纸Reference to the water supply drawings to be deepened by suppliers ，and provide chlorinated water recirculation pumping integration related parameters and installation drawings
18 | 保温罐INSULATED WATER TANKS | DIF |  | 容量Capacity ：2500 L ； 样式Model ：立式Vertical 按照CT要求配备压力计、温度表及必要的配件 Thermomet ers, manometers and all the accessories in compliance with the CT; 镁阳极防腐保护Anti-corrosion protection with a magnesium anode; 进行保温及机械防护Thermal insulation and mechanical protection; 立式固定和安装Fixations and supports for vertical installation; 排水阀门 Drain valves. | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： SANDOMETAL/ HOVAL 参看空调图纸，用于冷水管路Cold Water， 供应商予以深化并提供具体参数和安装尺寸It is used for Cold Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
19 | 保温罐INSULATED WATER TANKS | DAQ |  | 容量Capacity ：750 L ； 样式Model ：立式Vertical 按照CT要求配备压力计、温度表及必要的配件 Thermomet ers, manometers and all the accessories in compliance with the CT; 镁阳极防腐保护Anti-corrosion protection with a magnesium anode; 进行保温及机械防护Thermal insulation and mechanical protection; 立式固定和安装Fixations and supports for vertical installation; 排水阀门 Drain valves | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： SANDOMETAL/ HOVAL 参看空调图纸，用于热水管路HOT Water ，供应商予以深化并提供具体参数和安装尺寸It is used for Hot Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
20 | 机动膨胀水箱 MOTORIZED EXPANSION WATER Vessel | VE-F |  | 冷水容量Capacity ：750 L ； 电气性能Electric characteristics： 400V/3F/50Hz 功率power：1.1Kw 最大运行压力Maximum Operation Pressure：10bar 最高温度Maximum temperature：70℃ 样式Model ：立式Vertical 用于增压系统Compressor-controlled pressurization system; 配备自动断开阀、泄水阀、和截止阀Automatic cut-off valve, drain valve and sectioning valves; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：REFLEX / CALEFFI 参看空调图纸，用于冷水管路Cold Water， 供应商予以深化并提供具体参数和安装尺寸It is used for Cold Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
21 | 静态隔膜膨胀水箱 STATIC DIAPHRAGM EXPANSION WATER TANKS | VE-Q |  | 热水容量Capacity ：200 L ； 电气性能Electric characteristics： 400V/3F/50Hz 功率power：1.1Kw 最大运行压力Maximum Operation Pressure：6bar 最高温度Maximum temperature：70℃ 样式Model ：立式Vertical 隔膜式Membrane; 配备自动断开阀、泄水阀、和截止阀Automatic cut-off valve, drain valve and sectioning valves; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND：REFLEX / CALEFFI 参看空调图纸，用于热水管路HOT Water ，供应商予以深化并提供具体参数和安装尺寸It is used for Hot Water,Supplier Deepens the drawinngs and Provide Specific Parameters and Mounting Dimensions
22 | 生活水换热器INSULATED WATER TANKS – DOMESTIC HOT WATER (DHW) | DAQS |  | 容量Capacity ：1000 L ； 电加热器 Electric Heat Exchanger [kW]：15 名义压力 Nominal Pressure [bar] ：8 最高温度Maximum Temperature [ºC] ：100 样式Model ：立式Vertical 不锈钢罐壁Stainless steel walls; 不锈钢内盘管 Stainless Steel coil; 按CT要求配压力表温度计Thermometers, manometers and all the accessories accordingly with the CT; 镁阳极防腐保护Anti-corrosion protection with a magnesium anode； 保温及外壁机械防护Thermal insulation and mechanical protection; 样式Model ：立式Vertical | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： SANDOMETAL / ZANI /VULCANO
说明notes： |  |  |  | The item No.1,2,3,4,5,18,19,20,21,22 is used for air congditioning system ,the item No.6,7, is used for water supply system .

## 水泵控制箱招标 (hidden)
序号No. | 名称definition | 水泵图例legend for pumps | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
10 | 二次加热回路变速管道泵控制箱Electric Switchboard For The SECONDARY HEATING CIRCUIT Variable Speed IN - LINE Pumps | BDQ |  | 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 1
11 | 二次制冷回路变速管道泵控制箱Electric Switchboard For The SECUNDARY COOLING CIRCUIT Variable Speed IN - LINE Pumps | BDF |  | 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 1
12 | 一次加热回路定速管道泵控制箱Electric Switchboard For The PRIMARY HEATING CIRCUIT Constant Speed IN - LINE Pumps | BPQ |  | 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 1
13 | 一次制冷回路定速管道泵控制箱Electric Switchboard For The PRIMARY COOLING CIRCUIT Constant Speed IN - LINE Pumps | BPF |  | 电气控制箱主要性能 The Pumps will be supplied with an electric switchboard with the following main characteristics: 能对泵调节和管理Regulation and adjustment; 能声音报警 Audio alarm; 能报警恢复 Alarm reset; 有PMU2000水泵管理器Pump management unit – PMU2000; 有与楼宇自控系统进行远程通信的RS485总线接口 Possibility for remote communication with the building centralized management system, by BUS RS485; 有启动停止和自动运行开关Switches for Start/Stop/Automatic operation; 有水泵工作强度工作状态和系统故障的可视化信号Visual signalization for the working tension, pump working state and unit malfunctions; | 合格qualified | CE | 台un | 1

## fan通风机招标 (hidden)
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
26 | 油烟净化器ELECTROSTATIC FILTER MODULE | MFE–H | FEI7000 | 最大风量Air Flow Rate [m 3 /h] ：6750 最大压力损失Maximum Load Loss [Pa] ：100 | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR
27 | 变速油烟排气风机Variable Speed Plug HOTTE EXHAUST FAN | VEX-H |  | 风量Air Flow Rate [m 3 /h]： 6750 静压Static Pressure [Pa]：600 电机功率Motor Power [kW] ：3.0 声压级Sound Pressure Level dB (A) ：≤ 62 电机外置 Motor out of flow 三相电机Three-phase motor (400V/3F/50Hz) 防火等级Fire proof grade ：400°C/2H 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮和运行状态显示器Local stop push button and functioning state display; 带压差开关Differential air pressure switch; 变速控制器靠近油烟机安装 Speed variation controller to be installed near the Hotte | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
28 | 加压恒速轴流风机PRESSURIZATION Constant Speed Axial Fan | VPE |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：200 电机功率Motor Power [kW] ：0.55 防火等级Fire proof grade： 400°C/2H 三相电机Three-phase motor：400V/3F/50Hz 带长外壳Long casing 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 3 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
29 | 加压恒速轴流风机PRESSURIZATION Constant Speed Axial Fan | VPAC |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：200 电机功率Motor Power [kW] ：0.55 防火等级Fire proof grade： 400°C/2H 三相电机Three-phase motor：400V/3F/50Hz 带长外壳Long casing 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 2 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
30 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-0.3 |  | 风量Air Flow Rate [m 3 /h]： 1750 静压Static Pressure [Pa]：160 电机功率Motor Power [kW] ：0.32 单相电机Single-phase motor：230V/1F/50Hz 室内安装Indoor Installation 带吊装减震器Anti-Vibration suspensions; 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
31 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-C |  | 风量Air Flow Rate [m 3 /h]： 3420 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.75 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
32 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-B |  | 风量Air Flow Rate [m 3 /h]： 240 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.06 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
33 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-7.1 |  | 风量Air Flow Rate [m 3 /h]： 200 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.06 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
34 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-R |  | 风量Air Flow Rate [m 3 /h]： 2160 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.65 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
35 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-CZ |  | 风量Air Flow Rate [m 3 /h]： 660 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.45 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
36 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-0.1 |  | 风量Air Flow Rate [m 3 /h]： 345 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.08 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
37 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-0.2 |  | 风量Air Flow Rate [m 3 /h]： 1150 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.45 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
38 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-IS1 |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：250 电机功率Motor Power [kW] ：0.75 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments
39 | 恒速离心排气风机Constant Speed Centrifugal EXHAUST FAN | VEX-IS2 |  | 风量Air Flow Rate [m 3 /h]： 3600 静压Static Pressure [Pa]：200 电机功率Motor Power [kW] ：0.75 单相电机Single-phase motor：230V/1F/50Hz 室外安装Outdoor Installation 带地面减震器Supports with vibration isolators 带就地维修停机按钮Local stop push button | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR / S&P 风机内外组成元件必须防腐处理，以适应近海环境The Fans must include an anticorrosion treatment, for their internal and external components, specific for near sea environments

## thermal meter (hidden)
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
16 | 热能表 Thermal Meter | CEF — DN200 | DN250 | 规格 specification：DN250 型号Model：具体型号由厂家确定All models must be confirmed with the equipment supplier. 配备带脉冲能够控制器的水量流量计，包括脉冲输出Volume flow meter with impulse controller, including impulse exit; 用于热能的微处理器，内置显示屏并有M-BUS出口（至少有2个独立的出口），Microprocessors for thermal energy, with built-in display and equipped with M-BUS exit (with a minimum of 2 independent exits) 有电缆和温度探头（分配和返回），组合热电偶Cables and temperature probes (distribution and return), and built-up thermowells; | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：ZENNER / MINOL 安装在冷水指定回路上，法兰连接The thermal energy meters will be installed in the cooling circuits, as specified in the drawings 。Flange connection
17 | 热能表 Thermal Meter | CEQ — DN100 | DN125 | 规格 specification：DN125 型号Model：具体型号由厂家确定All models must be confirmed with the equipment supplier. 配备带脉冲能够控制器的水量流量计，包括脉冲输出Volume flow meter with impulse controller, including impulse exit; 用于热能的微处理器，内置显示屏并有M-BUS出口（至少有2个独立的出口），Microprocessors for thermal energy, with built-in display and equipped with M-BUS exit (with a minimum of 2 independent exits) 有电缆和温度探头（分配和返回），组合热电偶Cables and temperature probes (distribution and return), and built-up thermowells; | 合格qualified | CE | 台un | 2 | 参考品牌BRAND：ZENNER / MINOL 安装在热水指定回路上，法兰连接The thermal energy meters will be installed in the heating circuits, as specified in the drawings 。Flange connection

## COMMAND AND CONTROL POST (hidden)
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
15 | 湿式报警阀组集成COMMAND AND CONTROL POST |  | DN100 | 包括湿式报警阀本体,压力开关，水力警铃，过滤器，带锁阀门，延迟器，排水阀，警铃实验阀，上、下腔压力表，以及正确执行报警任务所必须的弯头、三通等管件、镀锌管等。Command and control post by levels, including safety valves, accessories, connections (hydraulic, electrical, fire, control etc) all materials and work needed to perfect and complete operation. Technical requirements, manufacturer and construction details according to specifications and drawings provided. | 合格qualified | CE | 台un | 2 | 参考消防水图纸，供应商予以深化，并提供湿式报警阀组的相关参数和安装图纸Reference fire water drawings to be deepened by suppliers, and provide the relevant detailed parameters and installation drawings

## SMOKE EXHAUST - HOOD (hidden)
序号No. | 名称definition | 图例legend | 规格specification | 主要技术参数main parameters | 质量要求quality requirement | 认证certification | 单位unit | 工程量quantity | 备注说明remarks
24 | 油烟集气罩 SMOKE EXHAUST - HOOD | HOOD-1 | 4000x1200x500 | 排气量Flow exhaust [m 3 /h] ：6750 带不锈钢送风口和排风口stainless steel plenums for exhaust and air supply 带油脂回收阀Valves for grease recovery; 带檐Visors; 带暗装照明灯 Embedded light; 带组装和安装配件Accessories for fixation and assembly; | 合格qualified | CE | 台un | 1 | 参考品牌BRAND： FRANCE AIR 厨房设备，304不锈钢制作Kitchen equipment,Stainless Steel AISI 304 18/10