Requirement specification on purchase of the pump

1.	subject to purchase: pump of pos. 16.A091-1-4, 16.B091-1-4 (8 pieces).

2.	Technical parameters of the equipment:

2.1	Flow: 1800 m3/h (with Kn =1,2)

2.2	Head: 71 m

3.	Scope of delivery:

3.1. With frame and electric motor

3.2. With the frequency converter

3.3. The passport, the mounting and operating manual in Russian

4.	The short description of a flow diagram in which the purchased equipment will be installed:

-	it is intended to supply solvent alkali liquor for heating and then into solvents;

-	it is installed in heated space.

5.	Special requirements to equipment:

-	the work mode: 300 days in a year, 24 hours a day;

-	ambient temperature, °C:	18-20;

-	relative air humidity: 60-75%;

-	climatic execution: U (-45/+40C).

6.	Criteria for the choice of the best proposal:

-	compliance with requirements of the requirement specification;

-	warranty service life;

-	power efficiency.

7.	The list of parameters, as the basic data necessary for development of the design documentation:

Characteristic of a working environment(medium):

- Solvent alkali liquor

Chemical composition:

KCl		12.19%

NaCl		17.20%

MgCl2		1.15%

CaCl2		2.30%

CaSO4		0.50%

H2o		66.66%.

Solids

-	size, mm		-

-	concentration, %	-

-	abrasivity		-

Operating temperature, °C: 			75.2

Density at operating temperature, kg/m3: 	1200

Pump inlet pressure, kgf/cm2: 		0.04-0.9