## 进口非金属阀门
label | function | nom. diameter | nom. pressure | description | material housing | material in contact with medium | Material Sealing | process connection | Safety position | instruments | pipe | material pipe section | medium
3112.V02-QM10 | OV 气动 | DN 15 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 319WP056 | PP | 1.01 Potable water | 1
3112.V10-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | BG12 / KK10 | 571WP190 | PP | 6.97 Waste mixed acid | 1
3112.V36-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | BG12 / KK10 | 311WP027 | PVDF | 6.37 Regenerated Mixed acid | 1
3112.V81-KJ01 | PIC | DN 40 | PN 10 | Pressure Reducer Straight-Way Valve 减压阀 | PP | PP | EPDM | flanged 法兰式 | -- |  | 311WP072 | PP | 1.01 Potable water | 1
3112.V83-QM10 | OV 气动 | DN 50 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | BG12 / KK10 | 311WP072 | PP | 1.01 Potable water | 1
3112.V89-QM10 | OV 气动 | DN 32 | PN 16 | Ball Valve 球阀 | PP | PP | FPM | spigot end | Open | BG12 / KK10 | 311WP041 | PP | 1.90 Waste water | 1
3112.V90-QM23 | HV 手动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP005 | PVDF | 6.47 Concentrated mixed acid | 1
3112.V90-QM24 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 311WP004 | PP | 6.47 Concentrated mixed acid | 1
3112.V91-RM26 | HV 手动 | DN 40 | PN 16 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | flanged 法兰式 | -- |  | 313WP044 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V02-QM10 | OV 气动 | DN 15 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 313WP046 | PP | 1.01 Potable water | 1
3131.V10-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 313WP045 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V11-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 313WP016 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V12-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 314WP054 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V20-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Open | BG11 / BG12 / KK10 | 313WP005 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V21-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 313WP036 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V90-QM10 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP009 | PP | 1.90 Waste water | 1
3131.V90-QM13 | HV 手动 | DN 15 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP013 | PP | 1.90 Waste water | 1
3131.V90-QM16 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP020 | PP | 1.90 Waste water | 1
3131.V90-QM17 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP026 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V90-QM18 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP038 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V91-RM05 | HV 手动 | DN 32 | PN 16 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | flanged 法兰式 | -- |  | 313WP016 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V10-QN01 | GC 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 314WP005 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V11-QM10 | OV 气动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK10 | 314WP003 | PP | 1.90 Waste water | 1
3141.V12-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK10 | 314WP016 | PP | 6.37 Regenerated Mixed acid | 1
3141.V20-QN01 | GC 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 314WP022 | PVDF | 6.58 Jet-scrubber acid | 1
3141.V34-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | EPDM | flanged 法兰式 | Closed | BG12 / KK10 | 314WP018 | PP | 1.90 Waste water | 1
3141.V90-QM05 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP010 | PP | 1.90 Waste water | 1
3141.V90-QM06 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP012 | PP | 1.90 Waste water | 1
3141.V90-QM07 | HV 手动 | DN 15 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP059 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V90-QM16 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP062 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V90-QM17 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP063 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V90-QM18 | HV 手动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP005 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V91-HL01 | HV 手动 | DN 40 | PN 10 | Filter 过滤器 | PVDF | PVDF | FPM | Butt welded 由令 | -- |  | 314WP005 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V91-RM01 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- |  | 314WP062 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V91-RM02 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- |  | 314WP063 | PVDF | 6.37 Regenerated Mixed acid | 1
3143.V10-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 316WP039 | PP | 1.67 Spray cooling water | 1
3143.V91-RM01 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- |  | 314WP064 | PVDF | 6.58 Jet-scrubber acid | 1
3143.V91-RM02 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- |  | 314WP065 | PVDF | 6.58 Jet-scrubber acid | 1
3161.V29-QN01 | GC 气动 | DN 20 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 3161WP01 | PP | 1.67 Spray cooling water | 1
3165.V10-QM10 | OV 气动 | DN 600 |  | Butterfly Valve 蝶阀(风阀) | PP | PP | FPM | between flanges 对夹式 | Closed | BG11 / BG12 / KK10 |  |  | 3.02 Combustion air
3165.V11-QM10 | OV 气动 | DN 300 |  | Butterfly Valve 蝶阀（风阀） | PP | PP | FPM | between flanges 对夹式 | Open | BG11 / BG12 / KK10 | 316WP034 | PP | 3.02 Combustion air | 1
3171.V11-QN01 | GC 气动 | DN 20 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 316WP047 | PP | 1.67 Spray cooling water | 1
3171.V20-QN01 | GC 气动 | DN 20 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 317WP016 | PP | 6.68 Oxidation column acid | 1
5627.V12-QM10 | OV 气动 | DN 40 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 562WP701 | PP | 1.90 Waste water | 1
5627.V22-QM10 | OV 气动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Open | KK10 | 562WP703 | PP | 1.90 Waste water | 1
5791.V10-QM10 | OV 气动 | DN 50 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 571WP397 | PP | 1.90 Waste water | 1
5791.V11-QM10 | OV 气动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Open | KK10 | 571WP396 | PP | 1.90 Waste water | 1

## 球阀
3112.V02-QM10 | OV 气动 | DN 15 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 319WP056 | PP | 1.01 Potable water
3112.V83-QM10 | OV 气动 | DN 50 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | BG12 / KK10 | 311WP072 | PP | 1.01 Potable water
3112.V89-QM10 | OV 气动 | DN 32 | PN 16 | Ball Valve 球阀 | PP | PP | FPM | spigot end | Open | BG12 / KK10 | 311WP041 | PP | 1.90 Waste water
3131.V02-QM10 | OV 气动 | DN 15 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 313WP046 | PP | 1.01 Potable water
5627.V12-QM10 | OV 气动 | DN 40 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 562WP701 | PP | 1.90 Waste water
5791.V10-QM10 | OV 气动 | DN 50 | PN 10 | Ball Valve 球阀 | PP | PP | FPM | Butt welded 由令 | Closed | KK10 | 571WP397 | PP | 1.90 Waste water

## 气动风阀
3165.V10-QM10 | OV 气动 | DN 600 | Butterfly Valve 蝶阀(风阀) | PP | PP | FPM | between flanges 对夹式 | Closed | BG11 / BG12 / KK10 |  |  | 3.02 Combustion air
3165.V11-QM10 | OV 气动 | DN 300 | Butterfly Valve 蝶阀（风阀） | PP | PP | FPM | between flanges 对夹式 | Open | BG11 / BG12 / KK10 | 316WP034 | PP | 3.02 Combustion air

## 隔膜阀
3112.V36-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | BG12 / KK10 | 311WP027 | PVDF | 6.37 Regenerated Mixed acid | 1
3112.V90-QM23 | HV 手动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP005 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V10-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 313WP045 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V11-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 313WP016 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V12-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 314WP054 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V20-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Open | BG11 / BG12 / KK10 | 313WP005 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V21-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 313WP036 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V90-QM17 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP026 | PVDF | 6.47 Concentrated mixed acid | 1
3131.V90-QM18 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP038 | PVDF | 6.47 Concentrated mixed acid | 1
3141.V10-QN01 | GC 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 314WP005 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V20-QN01 | GC 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | KK01 | 314WP022 | PVDF | 6.58 Jet-scrubber acid | 1
3141.V90-QM07 | HV 手动 | DN 15 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP059 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V90-QM16 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP062 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V90-QM17 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP063 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V90-QM18 | HV 手动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP005 | PVDF | 6.37 Regenerated Mixed acid | 1
3143.V10-QN01 | GC 气动 | DN 32 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 316WP039 | PP | 1.67 Spray cooling water | 1
3161.V29-QN01 | GC 气动 | DN 20 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 3161WP01 | PP | 1.67 Spray cooling water | 1
3171.V11-QN01 | GC 气动 | DN 20 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 316WP047 | PP | 1.67 Spray cooling water | 1
3171.V20-QN01 | GC 气动 | DN 20 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK01 | 317WP016 | PP | 6.68 Oxidation column acid | 1
5627.V22-QM10 | OV 气动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Open | KK10 | 562WP703 | PP | 1.90 Waste water | 1
5791.V11-QM10 | OV 气动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Open | KK10 | 571WP396 | PP | 1.90 Waste water | 1
3112.V90-QM24 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 311WP004 | PP | 6.47 Concentrated mixed acid | 1
3131.V90-QM10 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP009 | PP | 1.90 Waste water | 1
3131.V90-QM13 | HV 手动 | DN 15 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP013 | PP | 1.90 Waste water | 1
3131.V90-QM16 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 313WP020 | PP | 1.90 Waste water | 1
3141.V11-QM10 | OV 气动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK10 | 314WP003 | PP | 1.90 Waste water | 1
3141.V12-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | PTFE | flanged 法兰式 | Closed | KK10 | 314WP016 | PP | 6.37 Regenerated Mixed acid | 1
3141.V34-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PP | PP | EPDM | flanged 法兰式 | Closed | BG12 / KK10 | 314WP018 | PP | 1.90 Waste water | 1
3141.V90-QM05 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP010 | PP | 1.90 Waste water | 1
3141.V90-QM06 | HV 手动 | DN 25 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 |  |  | 314WP012 | PP | 1.90 Waste water | 1
3112.V10-QM10 | OV 气动 | DN 40 | PN 10 | Diaphragm Valve 隔膜阀 | PVDF | PVDF | PTFE | flanged 法兰式 | Closed | BG12 / KK10 | 571WP190 | PP | 6.97 Waste mixed acid | 1

## Y型过滤器
3141.V91-HL01 | HV 手动 | DN 40 | PN 10 | Filter Y型过滤器 | PVDF | PVDF | FPM | Butt welded 由令 | -- | 314WP005 | PVDF | 6.37 Regenerated Mixed acid | 1

## 立式止回阀
3112.V91-RM26 | HV 手动 | DN 40 | PN 16 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | flanged 法兰式 | -- | 313WP044 | PVDF | 6.37 Regenerated Mixed acid | 1
3131.V91-RM05 | HV 手动 | DN 32 | PN 16 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | flanged 法兰式 | -- | 313WP016 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V91-RM01 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- | 314WP062 | PVDF | 6.37 Regenerated Mixed acid | 1
3141.V91-RM02 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- | 314WP063 | PVDF | 6.37 Regenerated Mixed acid | 1
3143.V91-RM01 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- | 314WP064 | PVDF | 6.58 Jet-scrubber acid | 1
3143.V91-RM02 | HV 手动 | DN 25 | PN 10 | Globe Check Valve 球止回阀 | PVDF | PVDF | FPM | Butt welded 由令 | -- | 314WP065 | PVDF | 6.58 Jet-scrubber acid | 1

## 减压阀
3112.V81-KJ01 | PIC | DN 40 | PN 10 | Pressure Reducer Straight-Way Valve 减压阀 | PP | PP | EPDM | flanged 法兰式 | -- | 311WP072 | PP | 1.01 Potable water | 1