Cable Data Sheet

Product information

Description                             Cable 1P 20 AWG SHLD+1C18 AWG+2C16 AWG PVC JACKET

Special    characteristics     RoHS     compliant

| Cable construction |  |  |  |
| --- | --- | --- | --- |
| Conductor | Number of conductors | Twisted Pair 1 2 |  |
|  | Material | CuSn |  |
|  | Wire gauge | 20 AWG 18 AWG 16 AWG |  |
|  | Stranding | 10/30 AWG 16/30 AWG 26/30 AWG |  |
|  | Nominal conductor diameter | 0.036” 0.046” 0.059” |  |
|  | Material | PE Foam PVC RoHS |  |
|  | Nominal thickness | 0.025” 0.025” 0.020” |  |
| Insulation | Nominal wire diameter | 0.086” 0.096” 0.099” |  |
|  | Color | Brown & White | Blue Black &Red |
| Twisted Pair Shield | Tape | Aluminum Mylar |  |
|  | Drain | TC 24 AWG STR 7/32 |  |
| Other | Fillers | Paper and Polyvinyl Chloride(PVC)RoHS |  |
|  | Separator | Tissue Paper |  |
| Jacket | Material | Polyvinyl Chloride(PVC)RoHS |  |
|  | Nominal thickness | 0.072” |  |
|  | Nominal outside diameter | 0.445”±0.010” |  |
|  | Color | Black |  |

| Jacket print | HARTING,INC1PR20 AWG SHLD 60℃300V,1C18&2C16 AWG 600V 105℃ P/N 73550465972 SUN RES ROHS SF50C(SEQUENTIAL IN METERS) |  |
| --- | --- | --- |
| Certifications | Communication Cables | UL444/CSA C22.2 No.214 |
|  | Appliance Wiring Material | UL758/CSA C22.2 No.210.2 |
| Physical Characteristics | Weight approx. | 0.147 Kg/m |

| Performance characteristics |  |  |  |  |
| --- | --- | --- | --- | --- |
| Voltage Twisted Pair 300V/Conductors 600V |  |  |  |  |
| Electrical | Capacitance(Pair) | 42 pF±5 |  |  |
|  | Twisted Pair impedance | 120 Ohms±15 |  |  |
|  | Maximum resistance in Ohms/km@20℃ | 20 AWG/ 33.8 | 18 AWG/ 23.5 | 16 AWG/ 14.1 |
| Mechanical | Flammability rating | CSA FT2 |  |  |
|  | Minimum bend radius | 2.7 inches |  |  |
|  | Temperature range | 60℃ Pair,-20℃/105℃ |  |  |

ALUMINUM MYLAR

JACKET

FILLER

CONDUCTOR

TISSUE PAPER

DRAWING FOR REFERENCE ONLY