## Cover Sheet
FIREWATER PUMP PACKAGE DATASHEET
|  |  | Revision: R01 | Status: IFR
Document Type: DTS | System/Subsystem: NA | Discipline: MEC | Rev. Date: 14/August/2019
Contractor Document Number: |  |  | Page: 1 / 3
DETAILED ENGINEERING DESIGN, PROCUREMENT, CONSTRUCTION, INSTALLATION AND COMMISSIONING (EPCIC) OF A 100,000 BARREL CAPACITY CRUDE OIL BUFFER STORAGE TANK FACILITY FOR EGBEMA, EGBEMA-WEST AND UGADA FIELDS IN OML 20
FIREWATER PUMPS PACKAGE
DATA SHEET
R01 | IFR | 2019-08-14 | IFR | AIP | EA | SOO
A01 | IDC | 2019-06-21 | IDC | AIP | EA | SOO
Revision | Status | Date | Revision memo | Issued by | Checked by | Approved by

## FWM1
1 |  | Data/requisition sheet for | [17 empty] | Revision | The following lists are required for choice fields, do not delete
2 |  | FIREWATER MAIN PUMPS |  |  |  | PBA - 905A/B |  |  |  |  | Issued for Construction | [9 empty] | Issue Status ? | Single / Parallel Operation
3 |  | Applicable units of measurement : |  |  | SI units | [5 empty] | ( based on final process data ) | [9 empty] | Issued for Budget Proposals | ?
4 |  | Customer's reference | : | [6 empty] | Pump manufacturer |  |  | : | VTA | [6 empty] | Issued for Design | Single
5 |  | Location | : | EGBEMA FIELDS | [5 empty] | Pump type/size |  |  | : | VTA | [6 empty] | Issued for Combined Proposal | Parallel
6 |  | Number required | : | TWO (2) | [5 empty] | Manufacturers ref. # |  |  | : | VTA | [6 empty] | Issued for Construction
7 | OPERATING DATA | [19 empty] | Issued for Review | Continuous / Intermittent
8 |  | Pumped Liquid | : | Water | [5 empty] | Pumping temperature ( Normal ) | [6 empty] | : | 31 | deg C |  | Liquid Type 1 | ?
9 |  | H2S content | : | 0 |  |  |  | mg/kg |  | Pumping temperature ( Minimum ) | [6 empty] | : | 18 | deg C |  | ? | Continuous
10 |  | Liquid Type | : | Non-abrasive |  |  | Non-corrosive |  |  | Pumping temperature ( Maximum ) | [6 empty] | : | 35 | deg C |  | Abrasive | Intermittent
11 |  |  | : | Non-hazardous |  |  | No dissolved gas |  |  | Density at normal pumping temperature | [6 empty] | : | 1000 | kg/m3 |  | Non-abrasive
12 |  | Normal process Flow | : | 795 |  |  |  | m3/h |  | Viscosity at normal pumping temperature | [6 empty] | : | 0.7976 | mm2/s |  |  | Remote Starting
13 |  | Rated process Flow (VTC) | : | 874.5 |  |  |  | m3/h |  | Vapour pressure at normal pumping temperature | [6 empty] | : | 0.04242 | bara |  | dissolved | ?
14 |  | Minimum process flow (VTC) | : | 198.75 |  |  |  | m3/h |  | Pressure in suction vessel | [6 empty] | : | 1.0132 | bara |  |  | Yes
15 |  | Single / Parallel Operation | : | Parallel | [5 empty] | Pressure in discharge vessel | [6 empty] | : | 11 | bara |  |  | No
16 |  | Continuous / Intermittent | : | Intermittent | [5 empty] | Highest possible pressure in suction vessel | [6 empty] | : | 1.0132 | bara |  | Hazardous Category
17 |  | Remote starting | : | No | [5 empty] | Specific process conditions during start/stop/transients : | [10 empty] | Hazardous? | Service Category
18 |  | Service category | : | Essential | [16 empty] | Category 1 | ?
19 |  | Direction of rotation(VTC) | : | Clockwise ( facing pump drive end ) | [16 empty] | Category 2 | Vital
20 | PUMPING DATA (HOLD) | [19 empty] | Category 3 | Essential
21 |  | Head in suction vessel |  |  |  | : | 10.3323 | m liq.abs. |  | Head in discharge vessel | [6 empty] | : | 112.1688 | m liq.abs. |  | Non-hazardous | Non-essential
|  | Height of liquid in suction vessel above pump centre line (minus if below) |  |  | Max. |  | 7 | m |  | Max. height of liquid level in discharge vessel above pump centre line (minus if below) | [6 empty] | : | 18 | m
22 |  |  |  |  | Min. | : | 0.5 | m | [10 empty] | m
23 |  | Total head loss in suction line between suction vessel and pump |  |  |  | : | 1.57 | m liq. |  | Total head loss in discharge line between pump and discharge vessel plus loading arm operating head | [6 empty] | : | 16.255 | m liq.
24 |  | Total minimum suction head |  |  |  | : | 9.2623 | m liq.abs. |  | Total maximum discharge head | [6 empty] | : | 146.4238 | m liq.abs. |  | Rotation | Speed
25 |  | Head of vapour pressure |  |  |  | : | 0.43256 | m liq.abs. |  | Differential head at Rated flow | [6 empty] | : | 137.1615 | m liq. |  | ? | ?
26 |  | Minimum available NPSH |  |  |  | : | 8.8297 | m liq. |  | Estimated efficiency | [6 empty] | : | 75 | % |  | Clockwise ( facing pump drive end ) | Variable speed
27 |  | SITE CONDITIONS | [6 empty] | PUMP DRIVER | [11 empty] | Anti-clockwise ( facing pump drive end ) | Fixed speed
28 |  | Ambient temperature ( minimum ) |  |  |  | : | 18 | deg C |  | Pump power at estimated efficiency | [6 empty] | : | 396.191 | kW
29 |  | Ambient temperature ( maximum ) |  |  |  | : | 35 | deg C |  | Type |  |  |  |  | : | Combustion Engine |  |  |  |  | Winterisation / Tropicalisation | Transmission
30 |  | Winterisation / Tropicalisation required |  |  |  | : | Tropicalisation |  |  | Fixed / Variable Speed |  |  |  |  | : | Fixed speed |  |  |  |  | ? | ?
31 |  | Area classification | : | [6 empty] | Transmission |  |  |  |  | : | Direct drive |  |  |  |  | Winterisation | Direct drive
32 |  | Local Authority requirements : | [7 empty] | Estimated installed power ( +10%) |  |  |  |  | : |  |  | 435.8101 | kW |  | Tropicalisation | Gearbox drive
33 | [20 empty] | Not required | Fluid coupling
34 |  | COOLING WATER | [6 empty] | STEAM HEATING
35 |  | Chlorine content |  |  |  | : | NA | PPM |  | . | [8 empty] | . |  | Driver type | Steam Heating
36 |  | Maximum inlet temperature |  |  |  | : | NA | deg C |  | . | [8 empty] | . |  | ? | ?
37 |  | Maximum allowable outlet temperature |  |  |  | : | NA | deg C | ELECTRICAL SUPPLIES | [11 empty] | Electric Motor | Available
38 |  | Supply pressure |  |  |  | : | NA | bara |  | Electrical frequency | [6 empty] | : | 50 | Hz |  | Steam Turbine | Not available
39 |  | Return pressure |  |  |  | : | NA | bara |  | Voltage |  |  | : | N/A | Heaters |  | : | NA | Volts |  | Gas Turbine
40 |  | Fouling coefficient |  |  |  |  | NA | W/m2.K |  | Phase |  |  | : | NA | Heaters |  | : | NA | Volts |  | Combustion Engine | Frequency
41 |  | REMARKS | [19 empty] | ?
42 |  | 1) Max. estimated shut off discharge pressure based on Max. suction head and 10 % head rise | [14 empty] | : | 16.4958 | bara |  | Instrumentation | 50
43 |  | 2) Max. estimated shut off discharge pressure based on Max. suction head and 20 % head rise | [14 empty] | : | 17.8409 | bara |  | ? | 60
44 |  | 3) The Pump Power was determined using the Normal Flow Rate. | [18 empty] | A = Integral Field only
45 | [20 empty] | B = Integral Field + install materials | Liquid Type 2
46
47 | [20 empty] | Pumped Liquid
48 | [20 empty] | Dissolved gas?
49 | [20 empty] | No dissolved gas
50 | [20 empty] | Dissolved gases
51
52 | IDC | VTA - Vendor to Advise
53
54 |  | Selection of pump type shall be in accordance with NFPA 20
55 |  | Prepared by : Date : |  | Equipment : | FIREWATER MAIN PUMPS | [5 empty] | Rev. | 0 |  | A1 | B1 |  | C1 |  | E
56 |  | ASS 14/08/2019 | [8 empty] | Details | IDC |  | IFR | IFA |  | AFC
57 |  | Checked by : Date: |  | Plant : | EGBEMA WEST & UGADA FIELDS
58 |  | ESW 17/08/2019 | [8 empty] | Date | 2019-08-02 |  | 17/08/2019
59 |  | Approved by : Date: |  | Consignee : | [6 empty] | Signed
60 |  | A.O 24/08/2019
61 |  | Engineering by : |  | KGIS | [6 empty] | Equipment No. |  |  | PBA - 905A/B
62 |  | Principal : |  | NPDC | [6 empty] | Requisition No. |  |  | N/A
Sheet No. 2
|  | Units |  | SI |  |  | USC | [6 empty] | Select units?
|  | temperature |  | deg C |  |  | °F | [6 empty] | SI units
|  | flow |  | m3/h |  |  | GPM | [6 empty] | US customary units
|  | power |  | kW |  |  | BHP
|  | head |  | m liq.abs. |  |  | FT liq.abs.
|  | diff head |  | m liq. |  |  | FT liq.
|  | height |  | m |  |  | FT |  |  |  |  | Formulae |  | SI units |  |  |  | US units
|  | density |  | kg/m3 |  |  | SG |  |  |  |  | Suct head |  | 10.3323 |  |  |  | 0.0023372
|  | viscosity |  | mm2/s |  |  | Cp |  |  |  |  | Disch head |  | 112.1688 |  |  |  | 0.025373
|  | pressure |  | bara |  |  | PSIA |  |  |  |  | Vapour head |  | 0.43256 |  |  |  | 9.7849e-05
|  | specific heat |  | KJ/kg.deg K |  |  | BTU/LB°F |  |  |  |  | Shutoff pressure 10% |  | 16.4958 |  |  |  | 68445.2832
|  | Fouling coefficient |  | W/m2.K |  |  | BTU/FT2.°F |  |  |  |  | Shutoff pressure 20% |  | 17.8409 |  |  |  | 74391.6086
|  | length |  | mm |  |  | IN |  |  |  |  | Note 8
|  | weight |  | Kg |  |  | LBS |  |  |  |  | Power |  | 396.191 |  |  |  | 40444.9477
|  | Concentration |  | mg/kg |  |  | PPM |  |  |  |  | Power2 |  | #VALUE! |  |  |  | #VALUE!
|  | Gauge pressure |  |  |  |  | PSIG |  |  |  |  | RPM SS |  | 1800 |  |  |  | 1300
[12 empty] | RPM DS |  | 2500 |  |  |  | 1900
[12 empty] | NPSH rated |  | 6.8297 |  |  |  | 5.8297
[12 empty] | NPSH 120% |  | 8.5297 |  |  |  | 7.8297

## FWM2
1 |  | Data/requisition sheet for | [17 empty] | Revision | The following lists are required for choice fields, do not delete
2 |  | FIREWATER SPARE PUMP |  |  |  | PBA - 905C |  |  |  |  | Issued for Construction | [9 empty] | Issue Status ? | Single / Parallel Operation
3 |  | Applicable units of measurement : |  |  | SI units | [5 empty] | ( based on final process data ) | [9 empty] | Issued for Budget Proposals | ?
4 |  | Customer's reference | : | [6 empty] | Pump manufacturer |  |  | : | VTA | [6 empty] | Issued for Design | Single
5 |  | Location | : | EGBEMA FIELDS | [5 empty] | Pump type/size |  |  | : | VTA | [6 empty] | Issued for Combined Proposal | Parallel
6 |  | Number required | : | ONE (1) | [5 empty] | Manufacturers ref. # |  |  | : | VTA | [6 empty] | Issued for Construction
7 | OPERATING DATA | [19 empty] | Issued for Review | Continuous / Intermittent
8 |  | Pumped Liquid | : | Water | [5 empty] | Pumping temperature ( Normal ) | [6 empty] | : | 31 | deg C |  | Liquid Type 1 | ?
9 |  | H2S content | : | 0 |  |  |  | mg/kg |  | Pumping temperature ( Minimum ) | [6 empty] | : | 18 | deg C |  | ? | Continuous
10 |  | Liquid Type | : | Non-abrasive |  |  | Non-corrosive |  |  | Pumping temperature ( Maximum ) | [6 empty] | : | 35 | deg C |  | Abrasive | Intermittent
11 |  |  | : | Non-hazardous |  |  | No dissolved gas |  |  | Density at normal pumping temperature | [6 empty] | : | 1000 | kg/m3 |  | Non-abrasive
12 |  | Normal process Flow | : | 795 |  |  |  | m3/h |  | Viscosity at normal pumping temperature | [6 empty] | : | 0.7976 | mm2/s |  |  | Remote Starting
13 |  | Rated process Flow (VTC) | : | 874.5 |  |  |  | m3/h |  | Vapour pressure at normal pumping temperature | [6 empty] | : | 0.04242 | bara |  | dissolved | ?
14 |  | Minimum process flow (VTC) | : | 198.75 |  |  |  | m3/h |  | Pressure in suction vessel | [6 empty] | : | 1.0132 | bara |  |  | Yes
15 |  | Single / Parallel Operation | : | Parallel | [5 empty] | Pressure in discharge vessel | [6 empty] | : | 11 | bara |  |  | No
16 |  | Continuous / Intermittent | : | Intermittent | [5 empty] | Highest possible pressure in suction vessel | [6 empty] | : | 1.0132 | bara |  | Hazardous Category
17 |  | Remote starting | : | No | [5 empty] | Specific process conditions during start/stop/transients : | [10 empty] | Hazardous? | Service Category
18 |  | Service category | : | Essential | [16 empty] | Category 1 | ?
19 |  | Direction of rotation(VTC) | : | Clockwise ( facing pump drive end ) | [16 empty] | Category 2 | Vital
20 | PUMPING DATA (HOLD) | [19 empty] | Category 3 | Essential
21 |  | Head in suction vessel |  |  |  | : | 10.3323 | m liq.abs. |  | Head in discharge vessel | [6 empty] | : | 112.1688 | m liq.abs. |  | Non-hazardous | Non-essential
|  | Height of liquid in suction vessel above pump centre line (minus if below) |  |  | Max. |  | 7 | m |  | Max. height of liquid level in discharge vessel above pump centre line (minus if below) | [6 empty] | : | 18 | m
22 |  |  |  |  | Min. | : | 0.5 | m | [10 empty] | m
23 |  | Total head loss in suction line between suction vessel and pump |  |  |  | : | 1.57 | m liq. |  | Total head loss in discharge line between pump and discharge vessel plus loading arm operating head | [6 empty] | : | 16.255 | m liq.
24 |  | Total minimum suction head |  |  |  | : | 9.2623 | m liq.abs. |  | Total maximum discharge head | [6 empty] | : | 146.4238 | m liq.abs. |  | Rotation | Speed
25 |  | Head of vapour pressure |  |  |  | : | 0.43256 | m liq.abs. |  | Differential head at Rated flow | [6 empty] | : | 137.1615 | m liq. |  | ? | ?
26 |  | Minimum available NPSH |  |  |  | : | 8.8297 | m liq. |  | Estimated efficiency | [6 empty] | : | 75 | % |  | Clockwise ( facing pump drive end ) | Variable speed
27 |  | SITE CONDITIONS | [6 empty] | PUMP DRIVER | [11 empty] | Anti-clockwise ( facing pump drive end ) | Fixed speed
28 |  | Ambient temperature ( minimum ) |  |  |  | : | 18 | deg C |  | Pump power at estimated efficiency | [6 empty] | : | 396.191 | kW
29 |  | Ambient temperature ( maximum ) |  |  |  | : | 35 | deg C |  | Type |  |  |  |  | : | Electric Motor |  |  |  |  | Winterisation / Tropicalisation | Transmission
30 |  | Winterisation / Tropicalisation required |  |  |  | : | Tropicalisation |  |  | Fixed / Variable Speed |  |  |  |  | : | Fixed speed |  |  |  |  | ? | ?
31 |  | Area classification | : | [6 empty] | Transmission |  |  |  |  | : | Direct drive |  |  |  |  | Winterisation | Direct drive
32 |  | Local Authority requirements : | [7 empty] | Estimated installed power ( +10%) |  |  |  |  | : |  |  | 435.8101 | kW |  | Tropicalisation | Gearbox drive
33 | [20 empty] | Not required | Fluid coupling
34 |  | COOLING WATER | [6 empty] | STEAM HEATING
35 |  | Chlorine content |  |  |  | : | NA | PPM |  | . | [8 empty] | . |  | Driver type | Steam Heating
36 |  | Maximum inlet temperature |  |  |  | : | NA | deg C |  | . | [8 empty] | . |  | ? | ?
37 |  | Maximum allowable outlet temperature |  |  |  | : | NA | deg C | ELECTRICAL SUPPLIES | [11 empty] | Electric Motor | Available
38 |  | Supply pressure |  |  |  | : | NA | bara |  | Electrical frequency | [6 empty] | : | 50 | Hz |  | Steam Turbine | Not available
39 |  | Return pressure |  |  |  | : | NA | bara |  | Voltage |  |  | : | 415 | Heaters |  | : | NA | Volts |  | Gas Turbine
40 |  | Fouling coefficient |  |  |  |  | NA | W/m2.K |  | Phase |  |  | : | 3 | Heaters |  | : | NA | Volts |  | Combustion Engine | Frequency
41 |  | REMARKS | [19 empty] | ?
42 |  | 1) Max. estimated shut off discharge pressure based on Max. suction head and 10 % head rise | [14 empty] | : | 16.4958 | bara |  | Instrumentation | 50
43 |  | 2) Max. estimated shut off discharge pressure based on Max. suction head and 20 % head rise | [14 empty] | : | 17.8409 | bara |  | ? | 60
44 |  | 3) The Pump Power was determined using the Normal Flow Rate. | [18 empty] | A = Integral Field only
45 | [20 empty] | B = Integral Field + install materials | Liquid Type 2
46
47 | [20 empty] | Pumped Liquid
48 | [20 empty] | Dissolved gas?
49 | [20 empty] | No dissolved gas
50 | [20 empty] | Dissolved gases
51
52 | IDC | VTA - Vendor to Advise
53
54 |  | Selection of pump type shall be in accordance with NFPA 20
55 |  | Prepared by : Date : |  | Equipment : | FIREWATER SPARE PUMP | [5 empty] | Rev. | 0 |  | A1 | B1 |  | C1 |  | E
56 |  | ASS 14/08/2019 | [8 empty] | Details | IDC |  | IFR | IFA |  | AFC
57 |  | Checked by : Date: |  | Plant : | EGBEMA WEST & UGADA FIELDS
58 |  | ESW 17/08/2019 | [8 empty] | Date | 2019-08-02 |  | 17/08/2019
59 |  | Approved by : Date: |  | Consignee : | [6 empty] | Signed
60 |  | A.O 24/08/2019
61 |  | Engineering by : |  | KGIS | [6 empty] | Equipment No. |  |  | PBA - 905C
62 |  | Principal : |  | NPDC | [6 empty] | Requisition No. |  |  | N/A
Sheet No. 2
|  | Units |  | SI |  |  | USC | [6 empty] | Select units?
|  | temperature |  | deg C |  |  | °F | [6 empty] | SI units
|  | flow |  | m3/h |  |  | GPM | [6 empty] | US customary units
|  | power |  | kW |  |  | BHP
|  | head |  | m liq.abs. |  |  | FT liq.abs.
|  | diff head |  | m liq. |  |  | FT liq.
|  | height |  | m |  |  | FT |  |  |  |  | Formulae |  | SI units |  |  |  | US units
|  | density |  | kg/m3 |  |  | SG |  |  |  |  | Suct head |  | 10.3323 |  |  |  | 0.0023372
|  | viscosity |  | mm2/s |  |  | Cp |  |  |  |  | Disch head |  | 112.1688 |  |  |  | 0.025373
|  | pressure |  | bara |  |  | PSIA |  |  |  |  | Vapour head |  | 0.43256 |  |  |  | 9.7849e-05
|  | specific heat |  | KJ/kg.deg K |  |  | BTU/LB°F |  |  |  |  | Shutoff pressure 10% |  | 16.4958 |  |  |  | 68445.2832
|  | Fouling coefficient |  | W/m2.K |  |  | BTU/FT2.°F |  |  |  |  | Shutoff pressure 20% |  | 17.8409 |  |  |  | 74391.6086
|  | length |  | mm |  |  | IN |  |  |  |  | Note 8
|  | weight |  | Kg |  |  | LBS |  |  |  |  | Power |  | 396.191 |  |  |  | 40444.9477
|  | Concentration |  | mg/kg |  |  | PPM |  |  |  |  | Power2 |  | #VALUE! |  |  |  | #VALUE!
|  | Gauge pressure |  |  |  |  | PSIG |  |  |  |  | RPM SS |  | 1800 |  |  |  | 1300
[12 empty] | RPM DS |  | 2500 |  |  |  | 1900
[12 empty] | NPSH rated |  | 6.8297 |  |  |  | 5.8297
[12 empty] | NPSH 120% |  | 8.5297 |  |  |  | 7.8297

## FWM3
1 | [19 empty] | Revision |  | The following lists are required for choice fields, do not delete
2 |  | FIREWATER MAIN PUMPS |  |  |  | PBA - 905A/B |  |  |  |  | Issued for Construction | [10 empty] | Procurement procedure |  | Procurement procedure
3 | [10 empty] | ( based on final process data ) | [10 empty] | ? |  | ?
4 |  | Customer's ref | : | [18 empty] | Fully PI compliant |  | Apply PI agreement
5 |  | Manufacturer's ref. | : | VTA | [17 empty] | Modified PI product |  | Do not apply PI
6 |  | GENERAL INFORMATION |  |  |  |  | REQUISITION | [14 empty] | Engineered Solution
7 |  | Compliance with Procurement Initiative Manual
8 |  | Specification dated | [19 empty] | Basic Type |  | Configuration code |  | Configuration code |  | Configuration code
9 |  | DESIGN OPERATING CONDITIONS (VTA) |  |  |  |  | REQUISITION (VTC) | [14 empty] | ? | 1 | ? |  | ? |  | ?
10 |  | Pump speed (single/double suction impeller) |  |  |  | rpm | 3000 |  | / | 3000 |  |  |  | / |  |  |  | / |  |  | OH | Overhung | 2 | OH1 | 1 |  | 1
11 |  | Min. continuous flow (stable / thermal) |  |  |  | m3/h | by vendor | [13 empty] | BB | Between Bearings | 3 | OH2 | 2 |  | 2
12 |  | Rated Capacity |  |  |  | m3/h |  | 412.8 | [12 empty] | VS | Vertically Suspended | 4 | OH3 | 3 |  | 3
13 |  | Differential head at Normal capacity |  |  |  | m liq. |  | 86.3699 | [14 empty] | 5 | OH4 | 4 |  | 4
14 |  | Efficiency at normal capacity |  |  |  | % |  | 70 | [14 empty] | 6 | OH5 | 5 |  | 5
15 |  | Power absorbed at normal capacity |  |  |  | kW |  | 117.383 | [14 empty] | 7 | OH6 | 6 |  | 6
16 |  | Capacity at BEP (actual impeller size) |  |  |  | m3/h | by vendor | [17 empty] | 7 |  | 7
17 |  | Power absorbed at 120 % BEP |  |  |  | kW | by vendor | [14 empty] | Volute / Diffuser
18 |  | Recommended driver power |  |  |  | kW | by vendor | [14 empty] | ? |  | Volute / Diffuser
19 |  | Viscous correction factors |  |  | CQ/CH/CE |  | 0 | / | 0 | / | 0 |  | / |  | / |  | / |  | / |  |  | DEP 31.29.02.11 |  | ?
20 |  | NPSH required from Minimum to Rated capacity |  |  |  | m liq. |  | 9.1735 |  |  | Max. | [10 empty] | Single volute |  | Single volute
21 |  | NPSH required from Rated to 120% Rated capacity |  |  |  | m liq. |  | 9.8735 |  |  | Max. | [10 empty] | Double volute |  | Double volute
22 |  | PUMP DESIGN(VTC) |  |  |  |  | REQUISITION (VTC) | [14 empty] | Diffuser type |  | Diffuser type
23 |  | Pump model / frame / size : |  |  |  |  | by vendor
24 |  | = Basic Type ( Rotor ) |  |  |  |  | Overhung | [14 empty] | First Stage Suction |  | First Stage Suction
25 |  | = ISO 13709 configuration code |  |  |  |  | OH1 | [14 empty] | ? |  | ?
26 |  | = Single / Double volute / Diffuser |  |  |  |  | Single volute | [14 empty] | DEP 31.29.02.11 |  | Single suction
27 |  | = Single / Double suction (first stage) |  |  |  |  | Single suction | [14 empty] | Single suction |  | Double suction
28 |  | Number of stages |  |  |  |  | Minimum | [14 empty] | Double suction
29 |  | Max. / Actual / Min. impeller diameter |  |  |  | mm | by vendor | [5 empty] | / |  | / |  | / |  | /
30 |  | Max. allowable casing working pressure |  |  |  | bara | NFPA 20
31 |  | Max. allowable jacket / C.W. piping pressure |  |  |  | bara | NFPA 20
32 |  | Suction specific speed with max. impeller diameter at BEP (m3/h - m - rpm ) |  |  |  |  | Less than 12800
#REF! |  | MATERIALS OF CONSTRUCTION |  |  |  |  | REQUISITION
#REF! |  | Service Group / Material Group: |  |  |  |  | WATER |  | / | S1
#REF! |  | Casing |  |  |  |  | Cast Iron | [13 empty] | Casing |  | Cabon Steel
#REF! |  | Inner casing or volutes |  |  |  |  | Cast Iron | [13 empty] | Inner casing or volutes |  | Cast Iron
#REF! |  | Casing studs |  |  |  |  | Carbon Steel | [13 empty] | Casing studs |  | AISI 4140 Steel
#REF! |  | Min. wall thickness |  |  |  |  | - | [13 empty] | Min. wall thickness |  | -
#REF! |  | Cover |  |  |  |  | - | [13 empty] | Cover |  | -
#REF! |  | Casing gaskets |  |  |  |  | AUS spiral wound | [13 empty] | Casing gaskets |  | AUS Spiral wound (6)
#REF! |  | Wet bolting |  |  |  |  | Carbon Steel | [13 empty] | Wet bolting |  | Carbon Steel
#REF! |  | Bearing bracket |  |  |  |  | - | [13 empty] | Bearing |  | -
#REF! |  | Impeller |  |  |  |  | Cast Iron | [13 empty] | Bearing Housing |  | CS
#REF! |  | Impeller wear ring hardness |  |  |  |  | Cast Iron | [13 empty] | Impeller |  | Cast Iron
#REF! |  | Casing wear ring hardness |  |  |  |  | Cast Iron | [13 empty] | Impeller wear rings |  | Cast Iron
#REF! |  | Wear ring coating |  |  |  |  | - | [13 empty] | Casing wear ring hardness |  | Cast Iron
#REF! |  | Diffuser |  |  |  |  | - | [13 empty] | Diffuser |  | -
#REF! |  | Shaft |  |  |  |  | Carbon Steel | [13 empty] | Shaft |  | Carbon Steel
#REF! |  | Interstage shaft sleeve |  |  |  |  | Cast Iron | [13 empty] | Shaft Seal |  | AUS or 12% CHR
#REF! |  | Interstage bushing |  |  |  |  | Cast Iron | [13 empty] | Seal Gland |  | 316 AUS (5)
#REF! |  | Balance drum |  |  |  |  | - | [13 empty] | Interstage shaft sleeve |  | Cast Iron
#REF! |  | Balance ring |  |  |  |  | - | [13 empty] | Interstage bushing |  | Cast Iron
#REF! | IDC | Throat bushing |  |  |  |  | Cast Iron | [13 empty] | Drain Plug |  | -
#REF! |  | PRESSURE CONTAINING PARTS |  |  |  |  | REQUISITION | [13 empty] | Coupling |  | -
#REF! |  | Pump casing manufacturer |  |  |  |  | by vendor | [13 empty] | Coupling Guard |  | -
#REF! |  | Pump covers manufacturer |  |  |  |  | by vendor | [13 empty] | Flanges |  | -
#REF! | [20 empty] | Balance drum |  | -
#REF! | [20 empty] | Balance ring |  | -
#REF! | [20 empty] | Throat bushing |  | Cast Iron
#REF! | [20 empty] | Column / bowl Shaft bushings |  | filled Carbon
#REF! | [20 empty] | Dischage Head/ Suction can |  | Carbon Steel
#REF! |  | Engineering by : |  | KGIS | [7 empty] | Equipment No. |  |  |  | PBA - 905A/B
#REF! |  | Principal : |  | NPDC | [7 empty] | Requisition No. |  |  |  | N/A
Sheet No. 3

## FWM4
1 | [11 empty] | Revision | The following lists are required for choice fields, do not delete
2 |  | FIREWATER MAIN PUMPS |  |  | PBA - 905A/B |  |  | Issued for Construction |  |  |  |  | Lubrication | Lubrication
3 | [7 empty] | ( based on final process data ) |  |  |  |  | ? | ?
4 |  | Customer's ref | : | [9 empty] | Oil Bath | Oil Bath - splash
5 |  | Manufacturer's ref. | : | VTA | [8 empty] | Oil Mist | Oil Bath - ring
6 | WEIGHTS (VTA) |  |  |  |  | REQUISITION | [6 empty] | Force Feed Oil | Oil Mist - Purge
7 |  | Pump |  |  | Kg | by vendor | [7 empty] | Oil Mist - Pure
8 |  | Driver |  |  | Kg | by vendor | [7 empty] | Force Feed Oil
9 |  | Gearbox |  |  | Kg | N/A
10 |  | BEARINGS and LUBRICATION |  |  |  | REQUISITION
11 |  | Type of Lubrication : |  |  |  | Oil Bath
12 |  | Radial Bearings Type : |  |  |  | HI | [6 empty] | Bearing type
13 |  | Thrust Bearing Type : |  |  |  | HI | [6 empty] | ?
14 |  | Applicable lubrication |  |  |  | HI | [6 empty] | Rolling element | LO heating
15 |  | Constant Level Oiler : make / type / model | [10 empty] | Hydro-dynamic | ?
16 |  | Lube oil heating : |  |  |  | N/A | [7 empty] | Not required
17 |  | COOLING |  |  |  | REQUISITION | [6 empty] | Cooling medium | Steam
18 |  | Medium |  |  |  | Air cooling preferred | [6 empty] | ? | Electric
19 |  | Temp.(deg.C) / max. inlet pressure (bara) |  |  |  |  | / |  | / |  | / |  | Air cooling
20 |  | Cooling water piping material / API plan |  |  |  | Not applicable |  |  | / |  | / |  | Water cooling | Baseplate
21 |  | Cooling water flow to bearing housing(s) |  |  | m3/h | Not applicable | [7 empty] | ?
22 |  | PIPING |  |  |  | REQUISITION (VTC) | [6 empty] | Flange positions | Combined
23 |  | Suction : | size (mm)/ ANSI flange class |  |  | 300 | / | 150# | / |  | / |  | ? | Separate
24 |  |  | position facing driven end |  |  | End | [6 empty] | End | DEP 31.29.02.11
25 |  | Discharge : | size(mm) / ANSI flange class |  |  | 150 | / | 150# | / |  | / |  | Top | Not in scope
26 |  |  | position facing driven end |  |  | Top | [6 empty] | Right side
27 |  | ACCESSORIES |  |  |  | REQUISITION | [6 empty] | Left side | Foundation bolts
28 |  | Base plate : |  |  |  | Combined | [6 empty] | Vendor standard | ?
29 |  | Foundation bolts : |  |  |  | Required | [7 empty] | Required
30 |  | Coupling - make / type : |  |  |  | ISO | [6 empty] | Coupling | Not in scope
31 |  | Coupling guard - non-sparking : |  |  |  | ISO | [6 empty] | ?
32 |  | Vibration equipment connections |  |  |  | Not required | [6 empty] | API 610 | Vibration connections
33 |  | INSPECTION and TESTS |  |  |  | REQUISITION | [6 empty] | Not in scope | ?
34 |  | Inspection class | [11 empty] | Threaded connections
35 |  | Hydrostatic test |  |  |  | Certified | [6 empty] | Coupling guard | Flat surfaces
36 |  | Performance test |  |  |  | Certified | [6 empty] | ? | Not required
37 |  | NPSHR test ( if required by API 610) |  |  |  | Certified | [6 empty] | API 610
38 |  | Complete unit test ( if req'd by API 610) |  |  |  | Certified | [6 empty] | Not in scope | Inspection class
39 |  | Auxiliary equipment test |  |  |  | Certified | [7 empty] | ?
40 |  | Disassembly after test ( PI default is 'not required' ) |  |  |  | Not required | [6 empty] | Hydrotest | Class I
41 |  | Pump speed during performance test |  |  | rpm | Site speed | [6 empty] | ? | Class II
42 |  | Water test Capacity : ( required for VCC Pumps only ) |  |  | m3/h | by vendor | [6 empty] | Certified
43 |  | Water test Head : ( required for VCC Pumps only ) |  |  | m liq. | by vendor | [6 empty] | Observed | Perftest
44 |  | Water test Efficiency : ( required for VCC Pumps only ) |  |  | % | by vendor | [6 empty] | Witnessed | ?
45 |  | Water test Power : ( required for VCC Pumps only ) |  |  | kW | by vendor | [7 empty] | Certified
46 |  | Test bed / contract driver installed |  |  |  | Contract driver | [6 empty] | Testing | Observed
47 |  | Hydrostatic test pressure : casing / jackets / piping |  |  | bara | NFPA 20 | [6 empty] | ? | Witnessed
48 |  | Special tests | [10 empty] | Required | Not required
49 |  | VENDOR's DATA |  |  |  | REQUISITION | [6 empty] | Not required
50 |  | Scope of supply |  |  |  | NFPA 20 | [7 empty] | Disassembly after test
51 |  | General Arrangement drawing reference |  |  |  | by vendor | [6 empty] | Test driver | ?
52 |  | Cross sectional drawing reference |  |  |  | by vendor | [6 empty] | ? | Observed
53 | IDC | Interconnecting Piping Layout/Schematics reference |  |  |  | by vendor | [6 empty] | Test bed driver | Witnessed
54 |  | Performance curve reference |  |  |  | by vendor | [6 empty] | Contract driver | Not required
55 |  | Report on torsional analysis ( if analysis is required as per ISO 13709) |  |  |  | Required
56
57
58
59
60
61
62 |  | Engineering by : |  | KGIS |  |  |  | Equipment No. |  | PBA - 905A/B
63 |  | Principal : |  | NPDC |  |  |  | Requisition No. |  | N/A
Sheet No.4
Sheet No.4 continued on sheet No 5,6,7 & 8.

## JP1
1 |  | Data/requisition sheet for | [17 empty] | Revision | The following lists are required for choice fields, do not delete
2 |  | JOCKEY PUMPS |  |  |  | PBA - 904 |  |  |  |  | Issued for Construction | [9 empty] | Issue Status ? | Single / Parallel Operation
3 |  | Applicable units of measurement : |  |  | SI units | [5 empty] | ( based on final process data ) | [9 empty] | Issued for Budget Proposals | ?
4 |  | Customer's reference | : | [6 empty] | Pump manufacturer |  |  | : | VTA | [6 empty] | Issued for Firm Proposals | Single
5 |  | Location | : | Lagos, Nigeria | [5 empty] | Pump type/size |  |  | : | VTA | [6 empty] | Issued for Combined Proposal | Parallel
6 |  | Number required | : | ONE (1) | [5 empty] | Manufacturers ref. # |  |  | : | VTA | [6 empty] | Issued for Construction
7 | OPERATING DATA | [20 empty] | Continuous / Intermittent
8 |  | Pumped Liquid | : | Water | [5 empty] | Pumping temperature ( Normal ) (HOLD) | [6 empty] | : | 31 | deg C |  | Liquid Type 1 | ?
9 |  | H2S content | : | 0 |  |  |  | mg/kg |  | Pumping temperature ( Minimum ) (HOLD) | [6 empty] | : | 18 | deg C |  | ? | Continuous
10 |  | Liquid Type | : | Non-abrasive |  |  | Non-corrosive |  |  | Pumping temperature ( Maximum ) (HOLD) | [6 empty] | : | 35 | deg C |  | Abrasive | Intermittent
11 |  |  | : | Non-hazardous |  |  | No dissolved gas |  |  | Density at normal pumping temperature | [6 empty] | : | 995 | kg/m3 |  | Non-abrasive
12 |  | Normal process Flow | : | 17 |  |  |  | m3/h |  | Viscosity at normal pumping temperature | [6 empty] | : | 0.7976 | mm2/s |  |  | Remote Starting
13 |  | Rated process Flow (VTC) | : | 18.7 |  |  |  | m3/h |  | Vapour pressure at normal pumping temperature | [6 empty] | : | 0.04242 | bara |  | dissolved | ?
14 |  | Minimum process flow (VTC) | : | 4.25 |  |  |  | m3/h |  | Pressure in suction vessel | [6 empty] | : | 1.0132 | bara |  |  | Yes
15 |  | Single / Parallel Operation | : | Single | [5 empty] | Pressure in discharge vessel | [6 empty] | : | 11 | bara |  |  | No
16 |  | Continuous / Intermittent | : | Continuous | [5 empty] | Highest possible pressure in suction vessel | [6 empty] | : | 1.0132 | bara |  | Hazardous Category
17 |  | Remote starting | : | Yes | [5 empty] | Specific process conditions during start/stop/transients : | [10 empty] | Hazardous? | Service Category
18 |  | Service category | : | Essential | [16 empty] | Category 1 | ?
19 |  | Direction of rotation | : | Clockwise ( facing pump drive end ) | [16 empty] | Category 2 | Vital
20 | PUMPING DATA | [19 empty] | Category 3 | Essential
21 |  | Head in suction vessel |  |  |  | : | 10.3842 | m liq.abs. |  | Head in discharge vessel | [6 empty] | : | 112.7324 | m liq.abs. |  | Non-hazardous | Non-essential
|  | Height of liquid in suction vessel above pump centre line (minus if below) |  |  | Max. |  | 7 | m |  | Max. height of liquid level in discharge vessel above pump centre line (minus if below) | [6 empty] | : | 7 | m
22 |  |  |  |  | Min. | : | 0.45 | m | [10 empty] | m
23 |  | Total head loss in suction line between suction vessel and pump |  |  |  | : | 1.28 | m liq. |  | Total head loss in discharge line between pump and discharge vessel plus loading arm operating head | [6 empty] | : | 33.56 | m liq.
24 |  | Total minimum suction head |  |  |  | : | 9.5542 | m liq.abs. |  | Total maximum discharge head | [6 empty] | : | 153.2924 | m liq.abs. |  | Rotation | Speed
25 |  | Head of vapour pressure |  |  |  | : | 0.43474 | m liq.abs. |  | Differential head at Rated flow | [6 empty] | : | 143.7383 | m liq. |  | ? | ?
26 |  | Minimum available NPSH |  |  |  | : | 9.1195 | m liq. |  | Estimated efficiency | [6 empty] | : | 70 | % |  | Clockwise ( facing pump drive end ) | Variable speed
27 |  | SITE CONDITIONS | [6 empty] | PUMP DRIVER | [11 empty] | Anti-clockwise ( facing pump drive end ) | Fixed speed
28 |  | Ambient temperature ( minimum ) |  |  |  | : | 18 | deg C |  | Pump power at estimated efficiency | [6 empty] | : | 9.4648 | kW
29 |  | Ambient temperature ( maximum ) |  |  |  | : | 35 | deg C |  | Type |  |  |  |  | : | Electric Motor |  |  |  |  | Winterisation / Tropicalisation | Transmission
30 |  | Winterisation / Tropicalisation required |  |  |  | : | Tropicalisation |  |  | Fixed / Variable Speed |  |  |  |  | : | Fixed speed |  |  |  |  | ? | ?
31 |  | Area classification | : | [6 empty] | Transmission |  |  |  |  | : | Direct drive |  |  |  |  | Winterisation | Direct drive
32 |  | Local Authority requirements : | [7 empty] | Estimated installed power ( +10%) |  |  |  |  | : |  |  | 10.4113 | kW |  | Tropicalisation | Gearbox drive
33 | [20 empty] | Not required | Fluid coupling
34 |  | COOLING WATER | [6 empty] | STEAM HEATING | [8 empty] | Not available
35 |  | Chlorine content |  |  |  | : | NA | PPM |  | . | [8 empty] | . |  | Driver type | Steam Heating
36 |  | Maximum inlet temperature |  |  |  | : | NA | deg C |  | . | [8 empty] | . |  | ? | ?
37 |  | Maximum allowable outlet temperature |  |  |  | : | NA | deg C | ELECTRICAL SUPPLIES | [11 empty] | Electric Motor | Available
38 |  | Supply pressure |  |  |  | : | NA | bara |  | Electrical frequency | [6 empty] | : | 50 | Hz |  | Steam Turbine | Not available
39 |  | Return pressure |  |  |  | : | NA | bara |  | Voltage |  | Motors | : | 415 | Heaters |  | : | NA | Volts |  | Gas Turbine
40 |  | Fouling coefficient |  |  |  |  | NA | W/m2.K |  | Phase |  | Motors | : | 3 | Heaters |  | : | NA | Volts |  | Combustion Engine | Frequency
41 |  | REMARKS | [19 empty] | ?
42 |  | 1) Max. estimated shut off discharge pressure based on Max. suction head and 10 % head rise | [14 empty] | : | 17.1243 | bara |  | Instrumentation | 50
43 |  | 2) Max. estimated shut off discharge pressure based on Max. suction head and 20 % head rise | [14 empty] | : | 18.5268 | bara |  | ? | 60
44 |  | 3) The Pump Power was determined using the Normal Flow Rate. | [18 empty] | A = Integral Field only
45 | [20 empty] | B = Integral Field + install materials | Liquid Type 2
46 | [20 empty] | C = Field only to Principal's standards | ?
47 | [20 empty] | D = Field only to Vendor's standards | Corrosive
48 | [20 empty] | E = Full scope to Principal's standards | Non-corrosive
49 | [20 empty] | F = Full scope to Vendor's standards
50
51 | [20 empty] | Pumped Liquid
52 | IDC | [19 empty] | Dissolved gas?
53 | [20 empty] | No dissolved gas
54 | [20 empty] | Dissolved gases
55 |  | NA - Not Applicable
56 |  | VTA - Vendor to Advise
57 |  | VTC - Vendor to Confirm
58 |  | Selection of pump type shall be in accordance with API 610
59 |  | Prepared by : Date : |  | Equipment : | JOCKEY PUMPS | [5 empty] | Rev. | 1 |  | 2 | 3 |  | 4 |  | 5
60 |  | ASS 29/11/2017 | [8 empty] | Details | IDC |  | IFR | IFD
61 |  | Checked by : Date: |  | Plant : | EGBEMA WEST & UGADA FIELDS
62 |  | ASS 29/11/2017 | [8 empty] | Date | 2017-11-22 |  | 29/11/2017
63 |  | Approved by : Date: |  | Consignee : | NPDC | [5 empty] | Signed
64 |  | AO 29/11/2017
65 |  | Engineering by : |  | JIECL | [6 empty] | Equipment No. |  |  | PBA - 904
66 |  | Principal : |  | NPDC | [6 empty] | Requisition No. |  |  | N/A
Sheet No. 5
|  | Units |  | SI |  |  | USC | [6 empty] | Select units?
|  | temperature |  | deg C |  |  | °F | [6 empty] | SI units
|  | flow |  | m3/h |  |  | GPM | [6 empty] | US customary units
|  | power |  | kW |  |  | BHP
|  | head |  | m liq.abs. |  |  | FT liq.abs.
|  | diff head |  | m liq. |  |  | FT liq.
|  | height |  | m |  |  | FT |  |  |  |  | Formulae |  | SI units |  |  |  | US units
|  | density |  | kg/m3 |  |  | SG |  |  |  |  | Suct head |  | 10.3842 |  |  |  | 0.002349
|  | viscosity |  | mm2/s |  |  | Cp |  |  |  |  | Disch head |  | 112.7324 |  |  |  | 0.025501
|  | pressure |  | bara |  |  | PSIA |  |  |  |  | Vapour head |  | 0.43474 |  |  |  | 9.834e-05
|  | specific heat |  | KJ/kg.deg K |  |  | BTU/LB°F |  |  |  |  | Shutoff pressure 10% |  | 17.1243 |  |  |  | 71223.6966
|  | Fouling coefficient |  | W/m2.K |  |  | BTU/FT2.°F |  |  |  |  | Shutoff pressure 20% |  | 18.5268 |  |  |  | 77423.9844
|  | length |  | mm |  |  | IN |  |  |  |  | Note 8
|  | weight |  | Kg |  |  | LBS |  |  |  |  | Power |  | 9.4648 |  |  |  | 966.2121
|  | Concentration |  | mg/kg |  |  | PPM |  |  |  |  | Power2 |  | #VALUE! |  |  |  | #VALUE!
|  | Gauge pressure |  |  |  |  | PSIG |  |  |  |  | RPM SS |  | 12900 |  |  |  | 9800
[12 empty] | RPM DS |  | 18200 |  |  |  | 13900
[12 empty] | NPSH rated |  | 7.1195 |  |  |  | 6.1195
[12 empty] | NPSH 120% |  | 8.8195 |  |  |  | 8.1195

## JP2
1 | [19 empty] | Revision |  | The following lists are required for choice fields, do not delete
2 |  | JOCKEY PUMPS |  |  |  | PBA - 904 |  |  |  |  | Issued for Construction | [10 empty] | Procurement procedure |  | Procurement procedure
3 | [10 empty] | ( based on final process data ) | [10 empty] | ? |  | ?
4 |  | Customer's ref | : | [18 empty] | Fully PI compliant |  | Apply PI agreement
5 |  | Manufacturer's ref. | : | VTA | [17 empty] | Modified PI product |  | Do not apply PI
6 |  | GENERAL INFORMATION |  |  |  |  | REQUISITION | [14 empty] | Engineered Solution
7 |  | Compliance with Procurement Initiative Manual
8 |  | Specification dated | [19 empty] | Basic Type |  | Configuration code |  | Configuration code |  | Configuration code
9 |  | DESIGN OPERATING CONDITIONS |  |  |  |  | REQUISITION (VTC) | [14 empty] | ? | 1 | ? |  | ? |  | ?
10 |  | Pump speed (single/double suction impeller) |  |  |  | rpm |  |  | / |  |  |  |  | / |  |  |  | / |  |  | OH | Overhung | 2 | OH1 | 1 |  | 1
11 |  | Min. continuous flow (stable / thermal) |  |  |  | m3/h | VTA | [13 empty] | BB | Between Bearings | 3 | OH2 | 2 |  | 2
12 |  | Rated Capacity |  |  |  | m3/h |  | 18.7 | [12 empty] | VS | Vertically Suspended | 4 | OH3 | 3 |  | 3
13 |  | Differential head at Normal capacity |  |  |  | m liq. |  | 143.7383 | [14 empty] | 5 | OH4 | 4 |  | 4
14 |  | Efficiency at normal capacity |  |  |  | % |  | 70 | [14 empty] | 6 | OH5 | 5 |  | 5
15 |  | Power absorbed at normal capacity |  |  |  | kW |  | 9.4648 | [14 empty] | 7 | OH6 | 6 |  | 6
16 |  | Capacity at BEP (actual impeller size) |  |  |  | m3/h | VTA | [17 empty] | 7 |  | 7
17 |  | Power absorbed at 120 % BEP |  |  |  | kW | VTA | [14 empty] | Volute / Diffuser
18 |  | Recommended driver power |  |  |  | kW | VTA | [14 empty] | ? |  | Volute / Diffuser
19 |  | Viscous correction factors |  |  | CQ/CH/CE |  | 0 | / | 0 | / | 0 |  | / |  | / |  | / |  | / |  |  | DEP 31.29.02.11 |  | ?
20 |  | NPSH required from Minimum to Rated capacity |  |  |  | m liq. |  | 7.1195 |  |  | Max. | [10 empty] | Single volute |  | Single volute
21 |  | NPSH required from Rated to 120% Rated capacity |  |  |  | m liq. |  | 8.8195 |  |  | Max. | [10 empty] | Double volute |  | Double volute
22 |  | PUMP DESIGN |  |  |  |  | REQUISITION (VTC) | [14 empty] | Diffuser type |  | Diffuser type
23 |  | Pump model / frame / size : |  |  |  |  | by vendor
24 |  | = Basic Type ( Rotor ) |  |  |  |  | Overhung | [14 empty] | First Stage Suction |  | First Stage Suction
25 |  | = ISO 13709 configuration code |  |  |  |  | OH1 | [14 empty] | ? |  | ?
26 |  | = Single / Double volute / Diffuser |  |  |  |  | Single volute | [14 empty] | DEP 31.29.02.11 |  | Single suction
27 |  | = Single / Double suction (first stage) |  |  |  |  | Single suction | [14 empty] | Single suction |  | Double suction
28 |  | Number of stages |  |  |  |  | Minimum | [14 empty] | Double suction
29 |  | Max. / Actual / Min. impeller diameter |  |  |  | mm | by vendor | [5 empty] | / |  | / |  | / |  | /
30 |  | Max. allowable casing working pressure |  |  |  | bara | API 610
31 |  | Max. allowable jacket / C.W. piping pressure |  |  |  | bara | API 610
32 |  | Suction specific speed with max. impeller diameter at BEP (m3/h - m - rpm ) |  |  |  |  | Less than 12800
33 |  | MECHANICAL SEAL & SEALING SYSTEM
34 |  | Seals and Sealing System shall be in accordance with requisition number :
35 |  | MATERIALS OF CONSTRUCTION |  |  |  |  | REQUISITION
36 |  | Service Group / Material Group: |  |  |  |  | Water |  | / | S5
37 |  | Casing |  |  |  |  | Cast Iron | [13 empty] | Casing |  | Cabon Steel
38 |  | Inner casing or volutes |  |  |  |  | Cast Iron | [13 empty] | Inner casing or volutes |  | Cast Iron
39 |  | Casing studs |  |  |  |  | Carbon Steel | [13 empty] | Casing studs |  | AISI 4140 Steel
40 |  | Min. wall thickness |  |  |  |  | - | [13 empty] | Min. wall thickness |  | -
41 |  | Cover |  |  |  |  | - | [13 empty] | Cover |  | -
42 |  | Casing gaskets |  |  |  |  | AUS spiral wound | [13 empty] | Casing gaskets |  | AUS Spiral wound (6)
43 |  | Wet bolting |  |  |  |  | Carbon Steel | [13 empty] | Wet bolting |  | Carbon Steel
44 |  | Bearing bracket |  |  |  |  | - | [13 empty] | Bearing |  | -
45 |  | Impeller |  |  |  |  | Cast Iron | [13 empty] | Bearing Housing |  | CS
46 |  | Impeller wear ring hardness |  |  |  |  | Cast Iron | [13 empty] | Impeller |  | Cast Iron
47 |  | Casing wear ring hardness |  |  |  |  | Cast Iron | [13 empty] | Impeller wear rings |  | Cast Iron
48 |  | Wear ring coating |  |  |  |  | - | [13 empty] | Casing wear ring hardness |  | Cast Iron
49 |  | Diffuser |  |  |  |  | - | [13 empty] | Diffuser |  | -
50 |  | Shaft |  |  |  |  | Carbon Steel | [13 empty] | Shaft |  | Carbon Steel
51 |  | Interstage shaft sleeve |  |  |  |  | Cast Iron | [13 empty] | Shaft Seal |  | AUS or 12% CHR
52 |  | Interstage bushing |  |  |  |  | Cast Iron | [13 empty] | Seal Gland |  | 316 AUS (5)
53 | IDC | Balance drum |  |  |  |  | - | [13 empty] | Interstage shaft sleeve |  | Cast Iron
54 |  | Balance ring |  |  |  |  | - | [13 empty] | Interstage bushing |  | Cast Iron
55 |  | Throat bushing |  |  |  |  | Cast Iron | [13 empty] | Drain Plug |  | -
56 |  | PRESSURE CONTAINING PARTS |  |  |  |  | REQUISITION | [13 empty] | Coupling |  | -
57 |  | Pump casing manufacturer |  |  |  |  | by vendor | [13 empty] | Coupling Guard |  | -
58 |  | Pump covers manufacturer |  |  |  |  | by vendor | [13 empty] | Flanges |  | -
59 | [20 empty] | Balance drum |  | -
60 | [20 empty] | Balance ring |  | -
61 | [20 empty] | Throat bushing |  | Cast Iron
62 | [20 empty] | Column / bowl Shaft bushings |  | filled Carbon
63 | [20 empty] | Dischage Head/ Suction can |  | Carbon Steel
64 |  | Engineering by : |  | KGIS | [7 empty] | Equipment No. |  |  |  | PBA - 904
65 |  | Principal : |  | NPDC | [7 empty] | Requisition No. |  |  |  | N/A
Sheet No.6

## JP3
1 | [11 empty] | Revision | The following lists are required for choice fields, do not delete
2 |  | JOCKEY PUMPS |  |  | PBA - 904 |  |  | Issued for Construction |  |  |  |  | Lubrication | Lubrication
3 | [7 empty] | ( based on final process data ) |  |  |  |  | ? | ?
4 |  | Customer's ref | : | [9 empty] | Oil Bath | Oil Bath - splash
5 |  | Manufacturer's ref. | : | VTA | [8 empty] | Oil Mist | Oil Bath - ring
6 | WEIGHTS |  |  |  |  | REQUISITION | [6 empty] | Force Feed Oil | Oil Mist - Purge
7 |  | Pump |  |  | Kg | VTA | [7 empty] | Oil Mist - Pure
8 |  | Driver |  |  | Kg | VTA | [7 empty] | Force Feed Oil
9 |  | Gearbox |  |  | Kg | VTA
10 |  | BEARINGS and LUBRICATION |  |  |  | REQUISITION
11 |  | Type of Lubrication : |  |  |  | Oil Bath
12 |  | Radial Bearings Type : |  |  |  | HI | [6 empty] | Bearing type
13 |  | Thrust Bearing Type : |  |  |  | HI | [6 empty] | ?
14 |  | Applicable lubrication |  |  |  | HI | [6 empty] | Rolling element | LO heating
15 |  | Constant Level Oiler : make / type / model |  |  |  | N/A | [6 empty] | Hydro-dynamic | ?
16 |  | Lube oil heating : |  |  |  | VTA | [7 empty] | Not required
17 |  | COOLING |  |  |  | REQUISITION | [6 empty] | Cooling medium | Steam
18 |  | Medium |  |  |  | Air cooling preferred | [6 empty] | ? | Electric
19 |  | Temp.(deg.C) / max. inlet pressure (bara) |  |  |  |  | / |  | / |  | / |  | Air cooling
20 |  | Cooling water piping material / API plan |  |  |  | Not applicable |  |  | / |  | / |  | Water cooling | Baseplate
21 |  | Cooling water flow to bearing housing(s) |  |  | m3/h | Not applicable | [7 empty] | ?
22 |  | PIPING |  |  |  | REQUISITION | [6 empty] | Flange positions | Combined
23 |  | Suction : | size (mm)/ ANSI flange class |  |  | 100 | / | 150# | / |  | / |  | ? | Separate
24 |  |  | position facing driven end |  |  | End | [6 empty] | End | DEP 31.29.02.11
25 |  | Discharge : | size(mm) / ANSI flange class |  |  | 80 | / | 150# | / |  | / |  | Top | Not in scope
26 |  |  | position facing driven end |  |  | Top | [6 empty] | Right side
27 |  | ACCESSORIES |  |  |  | REQUISITION | [6 empty] | Left side | Foundation bolts
28 |  | Base plate : |  |  |  | Combined | [6 empty] | Vendor standard | ?
29 |  | Foundation bolts : |  |  |  | Required | [7 empty] | Required
30 |  | Coupling - make / type : |  |  |  | API 610 | [6 empty] | Coupling | Not in scope
31 |  | Coupling guard - non-sparking : |  |  |  | API 610 | [6 empty] | ?
32 |  | Vibration equipment connections |  |  |  | Not required | [6 empty] | API 610 | Vibration connections
33 |  | INSPECTION and TESTS |  |  |  | REQUISITION | [6 empty] | Not in scope | ?
34 |  | Inspection class | [11 empty] | Threaded connections
35 |  | Hydrostatic test |  |  |  | Certified | [6 empty] | Coupling guard | Flat surfaces
36 |  | Performance test |  |  |  | Certified | [6 empty] | ? | Not required
37 |  | NPSHR test ( if required by API 610) |  |  |  | Certified | [6 empty] | API 610
38 |  | Complete unit test ( if req'd by API 610) |  |  |  | Certified | [6 empty] | Not in scope | Inspection class
39 |  | Auxiliary equipment test |  |  |  | Certified | [7 empty] | ?
40 |  | Disassembly after test ( PI default is 'not required' ) |  |  |  | Not required | [6 empty] | Hydrotest | Class I
41 |  | Pump speed during performance test |  |  | rpm | Site speed | [6 empty] | ? | Class II
42 |  | Water test Capacity : ( required for VCC Pumps only ) |  |  | m3/h | by vendor | [6 empty] | Certified
43 |  | Water test Head : ( required for VCC Pumps only ) |  |  | m liq. | by vendor | [6 empty] | Observed | Perftest
44 |  | Water test Efficiency : ( required for VCC Pumps only ) |  |  | % | by vendor | [6 empty] | Witnessed | ?
45 |  | Water test Power : ( required for VCC Pumps only ) |  |  | kW | by vendor | [7 empty] | Certified
46 |  | Test bed / contract driver installed |  |  |  | Contract driver | [6 empty] | Testing | Observed
47 |  | Hydrostatic test pressure : casing / jackets / piping |  |  | bara | API 610 | [6 empty] | ? | Witnessed
48 |  | Special tests | [10 empty] | Required | Not required
49 |  | VENDOR's DATA |  |  |  | REQUISITION | [6 empty] | Not required
50 |  | Scope of supply |  |  |  | NFPA 20 | [7 empty] | Disassembly after test
51 |  | General Arrangement drawing reference |  |  |  | VTA | [6 empty] | Test driver | ?
52 |  | Cross sectional drawing reference |  |  |  | VTA | [6 empty] | ? | Observed
53 | IDC | Interconnecting Piping Layout/Schematics reference |  |  |  | VTA | [6 empty] | Test bed driver | Witnessed
54 |  | Performance curve reference |  |  |  | VTA | [6 empty] | Contract driver | Not required
55 |  | Report on torsional analysis ( if analysis is required as per ISO 13709) |  |  |  | Required
56
57
58
59
60
61
62 |  | Engineering by : |  | KGIS |  |  |  | Equipment No. |  | PBA - 904
63 |  | Principal : |  | NPDC |  |  |  | Requisition No. |  | N/A
Sheet No. 7