## Valve list
| KKS Identification | Client P&ID Nº | Env | ND | Type | Material | Cat. Nº | Rating | End | Sch | Line | Fluid | Design |  | Fail Position | Drive | Acc. | Ins.Th | Datasheet | Specification | Client Specification | Paint System | Color RAL | Supplier | Manufacturer | Vacuum | Notes
[13 empty] | P(barg) | T(ºC)
1 | 01GHA99AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GHA99BR001 | Water | 9 | 46,5 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
2 | 01GHA99AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GHA99BR001 | Water | 9 | 46,5 |  |  | KW |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
3 | 01GHA99AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GHA99BR002 | Water | 9 | 46,5 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
4 | 01GHA99AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GHA99BR501 | Water | 9 | 46,5 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
5 | 01GHA99AA551 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GHA99BR551 | Water | 9 | 46,5 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
6 | 01LAE35AA501 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAE35BR501 | Feedwater | 275 | 100 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
7 | 01LAE35AA502 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAE35BR511 | Feedwater | 275 | 100 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
8 | 01LAE35AA503 | RDST-00-LB_-MDD-EAI-10200 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAE35BR503 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
9 | 01LAE35AA504 | RDST-00-LB_-MDD-EAI-10200 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAE35BR503 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
10 | 01LAE35AA505 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAE35BR505 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
11 | 01LAE35AA506 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAE35BR505 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
12 | 01LBQ59AA002 | RDST-00-LBD-MDD-EAI-10230 | I | 100 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LBQ59BR003 | Water-Steam | 17/vacuum | 470 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
13 | 01LBS10AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LBS10BR003 | Steam | 3.5/vacuum | 150 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
14 | 01LBS10AA702 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS10BR003 | Steam | 3.5/vacuum | 150 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
15 | 01LBS10AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS10BR003 | Steam | 3.5/vacuum | 150 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
16 | 01LBS10AA704 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LBS10BR003 | Steam | 3.5/vacuum | 150 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
17 | 01LBS11AA001 | RDST-00-LBD-MDD-EAI-10230 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS11BR002 | Water-Steam | 3.5/vacuum | 150 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
18 | 01LBS11AA501 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LBS11BR501 | Water-Steam | 3.5/vacuum | 150 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
19 | 01LBS20AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LBS20BR001 | Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
20 | 01LBS20AA702 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS20BR001 | Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
21 | 01LBS20AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LBS20BR001 | Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
22 | 01LBS20AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS20BR001 | Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
23 | 01LBS21AA101 | RDST-00-LBD-MDD-EAI-10230 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS21BR002 | Water-Steam | 3.5/vacuum | 210 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
24 | 01LBS21AA501 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LBS21BR501 | Water-Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
25 | 01LBS22AA101 | RDST-00-LBD-MDD-EAI-10230 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS22BR002 | Water-Steam | 3.5/vacuum | 210 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
26 | 01LBS22AA501 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LBS22BR501 | Water-Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
27 | 01LBS22AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS22BR001 | Water-Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
28 | 01LBS22AA702 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS22BR001 | Water-Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
29 | 01LBS22AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS22BR001 | Water-Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
30 | 01LBS22AA704 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS22BR001 | Water-Steam | 3.5/vacuum | 210 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
31 | 01LBS30AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LBS30BR001 | Steam | 4/vacuum | 400 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
32 | 01LBS30AA702 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS30BR001 | Steam | 4/vacuum | 400 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
33 | 01LBS30AA703 | RDST-00-LBD-MDD-EAI-10230 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS30BR001 | Steam | 4/vacuum | 400 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
34 | 01LBS30AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LBS30BR001 | Steam | 4/vacuum | 400 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
35 | 01LBS31AA101 | RDST-00-LBD-MDD-EAI-10230 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS31BR002 | Water-Steam | 4/vacuum | 400 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
36 | 01LBS31AA501 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LBS31BR501 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
37 | 01LBS32AA101 | RDST-00-LBD-MDD-EAI-10230 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS32BR002 | Water-Steam | 4/vacuum | 400 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
38 | 01LBS32AA502 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LBS32BR501 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
39 | 01LBS32AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS32BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
40 | 01LBS32AA702 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS32BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
41 | 01LBS32AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS32BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
42 | 01LBS32AA704 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS32BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
43 | 01LBS33AA101 | RDST-00-LBD-MDD-EAI-10230 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS33BR002 | Water-Steam | 4/vacuum | 400 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
44 | 01LBS33AA501 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LBS33BR501 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
45 | 01LBS33AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS33BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
46 | 01LBS33AA702 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS33BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
47 | 01LBS33AA703 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS33BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
48 | 01LBS33AA704 | RDST-00-LBD-MDD-EAI-10230 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LBS33BR001 | Water-Steam | 4/vacuum | 400 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
49 | 01LCA10AA002 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCA10BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
50 | 01LCA10AA003 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA10BR002 | Condensate | 37/-1 | 105 |  |  | BK | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
51 | 01LCA10AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA10BR501 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
52 | 01LCA10AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA10BR502 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
53 | 01LCA10AA701 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA10BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
54 | 01LCA10AA702 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA10BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
55 | 01LCA10AA703 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA10BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
56 | 01LCA10AA704 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA10BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
57 | 01LCA12AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA12BR001 | Air | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
58 | 01LCA20AA002 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCA20BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
59 | 01LCA20AA003 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA20BR002 | Condensate | 37/-1 | 105 |  |  | BK | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
60 | 01LCA20AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR501 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
61 | 01LCA20AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR502 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
62 | 01LCA20AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR551 | Air-Water | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
63 | 01LCA20AA701 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
64 | 01LCA20AA702 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
65 | 01LCA20AA703 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
66 | 01LCA20AA704 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA20BR001 | Condensate | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
67 | 01LCA22AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA22BR001 | Air | 3.5/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
68 | 01LCA27AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA27BR001 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
69 | 01LCA30AA004 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA30BR001 | Condensate | 37/-1 | 105 |  |  | BK | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
70 | 01LCA30AA006 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
71 | 01LCA30AA008 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve, closed | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA30BR005 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
72 | 01LCA30AA505 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR505 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
73 | 01LCA30AA506 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR506 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
74 | 01LCA30AA507 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR507 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
75 | 01LCA30AA552 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR552 | Air-Water | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
76 | 01LCA30AA701 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR001 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
77 | 01LCA30AA703 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
78 | 01LCA30AA705 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR001 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
79 | 01LCA30AA706 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
80 | 01LCA30AA708 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
81 | 01LCA30AA709 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
82 | 01LCA30AA710 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
83 | 01LCA30AA711 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA30BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
84 | 01LCA31AA501 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR501 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
85 | 01LCA31AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR502 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
86 | 01LCA31AA551 | RDST-00-LC_-MDD-EAI-10400 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR551 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
87 | 01LCA31AA552 | RDST-00-LC_-MDD-EAI-10400 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR552 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
88 | 01LCA31AA553 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01LCA31BR553 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
89 | 01LCA31AA701 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR001 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
90 | 01LCA31AA702 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR001 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
91 | 01LCA31AA703 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR002 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
92 | 01LCA31AA704 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR002 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
93 | 01LCA31AA705 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA31BR002 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
94 | 01LCA32AA001 | RDST-00-LC_-MDD-EAI-10400 | I | 200 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCA32BR002 | Condensate | 37/-1 | 148 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
95 | 01LCA32AA501 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR501 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
96 | 01LCA32AA551 | RDST-00-LC_-MDD-EAI-10400 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR551 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
97 | 01LCA32AA552 | RDST-00-LC_-MDD-EAI-10400 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR552 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
98 | 01LCA32AA553 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01LCA32BR553 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
99 | 01LCA32AA701 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR001 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
100 | 01LCA32AA702 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR001 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
101 | 01LCA32AA703 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR002 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
102 | 01LCA32AA704 | RDST-00-LC_-MDD-EAI-10400 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR002 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
103 | 01LCA32AA705 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA32BR002 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
104 | 01LCA33AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR501 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
105 | 01LCA33AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR502 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
106 | 01LCA33AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR551 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
107 | 01LCA33AA552 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR552 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
108 | 01LCA33AA553 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01LCA33BR553 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
109 | 01LCA33AA701 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR001 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
110 | 01LCA33AA702 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR001 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
111 | 01LCA33AA703 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR002 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
112 | 01LCA33AA704 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR002 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
113 | 01LCA33AA705 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA33BR002 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
114 | 01LCA34AA002 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA34BR007 | Condensate | 37/-1 | 196 |  |  | K | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
115 | 01LCA34AA003 | RDST-00-LC_-MDD-EAI-10400 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA34BR002 | Condensate | 37/-1 | 196 |  |  | K | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
116 | 01LCA34AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR501 | Condensate | 37/-1 | 196 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
117 | 01LCA34AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR502 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
118 | 01LCA34AA503 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR503 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
119 | 01LCA34AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR551 | Condensate | 20 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
120 | 01LCA34AA552 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR552 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
121 | 01LCA34AA553 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01LCA34BR553 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
122 | 01LCA34AA701 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR001 | Condensate | 37/-1 | 196 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
123 | 01LCA34AA702 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR001 | Condensate | 37/-1 | 196 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
124 | 01LCA34AA703 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR002 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
125 | 01LCA34AA704 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR002 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
126 | 01LCA34AA705 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR002 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
127 | 01LCA34AA706 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR007 | Condensate | 20 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
128 | 01LCA34AA707 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR002 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
129 | 01LCA34AA708 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR007 | Condensate | 20 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
130 | 01LCA34AA710 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR002 | Condensate | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
131 | 01LCA34AA711 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR007 | Condensate | 20 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
132 | 01LCA34AA712 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR007 | Condensate | 20 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
133 | 01LCA34AA713 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR007 | Condensate | 20 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
134 | 01LCA37AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA34BR004 | Condensate | 37/-1 | 196 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
135 | 01LCA40AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 150 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA40BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
136 | 01LCA45AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA45BR005 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
137 | 01LCA45AA701 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA45BR006 | Condensate | 4/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
138 | 01LCA50AA003 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA50BR004 | Condensate | 4/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
139 | 01LCA50AA004 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA50BR001 | Condensate | 4/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
140 | 01LCA50AA005 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCA50BR007 | Condensate | 4/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
141 | 01LCA50AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA50BR502 | Condensate | 4/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
142 | 01LCA60AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 150 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA60BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
143 | 01LCA60AA002 | RDST-00-LC_-MDD-EAI-10400 | E | 150 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA60BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
144 | 01LCA60AA301 | RDST-00-LC_-MDD-EAI-10400 | E | 150 mm | Globe valve, closed | A-216 Gr WCB | AB1TB | CL300 | BW | STD | 01LCA60BR002 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
145 | 01LCA60AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA60BR501 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
146 | 01LCA60AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA60BR502 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
147 | 01LCA60AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA60BR551 | Air-Water | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
148 | 01LCA60AA552 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA60BR552 | Air-Water | 10/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
149 | 01LCA70AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 100 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA70BR001 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
150 | 01LCA70AA003 | RDST-00-LC_-MDD-EAI-10400 | E | 100 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCA70BR001 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
151 | 01LCA70AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA70BR501 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
152 | 01LCA70AA502 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA70BR502 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
153 | 01LCA70AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCA70BR551 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
154 | 01LCA80AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 50 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LCA80BR002 | Condensate | 275 | 211 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
155 | 01LCA80AA003 | RDST-00-LC_-MDD-EAI-10400 | E | 50 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LCA80BR002 | Condensate | 275 | 211 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
156 | 01LCC10AA501 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR501 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
157 | 01LCC10AA551 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR551 | Air-Water | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
158 | 01LCC10AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Steam | 3.5/vacuum | 150 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
159 | 01LCC20AA501 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR501 | Condensate | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
160 | 01LCC20AA551 | RDST-00-LC_-MDD-EAI-10400 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR551 | Air-Water | 37/-1 | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
161 | 01LCC20AA709 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Steam | 3.5/vacuum | 210 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
162 | 01LCC30AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR501 | Condensate | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
163 | 01LCC30AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR551 | Air-Water | 37/-1 | 172 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
164 | 01LCC30AA701 | RDST-00-LBD-MDD-EAI-10230 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Steam | 4/vacuum | 400 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
165 | 01LCC40AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR501 | Condensate | 37/-1 | 196 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
166 | 01LCC40AA551 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR551 | Air-Water | 37/-1 | 196 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
167 | 01LCE01AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE01BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
168 | 01LCE03AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE03BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
169 | 01LCE03AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE03BR501 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
170 | 01LCE04AA501 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE04BR501 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
171 | 01LCE05AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE05BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
172 | 01LCE06AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE06BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
173 | 01LCE06AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE06BR501 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
174 | 01LCE07AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE07BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
175 | 01LCE07AA501 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE07BR501 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
176 | 01LCE08AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE08BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
177 | 01LCE09AA001 | RDST-00-LC_-MDD-EAI-10400 | I | 150 mm | Globe Valve | A-216 Gr WCB | AB1TB | CL300 | BW | STD | 01LCE09BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
178 | 01LCE30AA001 | RDST-00-LC_-MDD-EAI-10400 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE30BR002 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
179 | 01LCE60AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE60BR002 | Condensate | 37/vacuum | 105 |  |  | BK |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
180 | 01LCE60AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE60BR002 | Condensate | 37/vacuum | 105 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
181 | 01LCE60AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE60BR003 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
182 | 01LCE60AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE60BR501 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
183 | 01LCE60AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE60BR502 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
184 | 01LCE60AA550 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE60BR550 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
185 | 01LCE70AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE70BR002 | Condensate | 37/vacuum | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
186 | 01LCE70AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE70BR002 | Condensate | 37/vacuum | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
187 | 01LCE70AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE70BR003 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
188 | 01LCE70AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE70BR501 | Condensate | 37/vacuum | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
189 | 01LCE70AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE70BR502 | Condensate | 37/vacuum | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
190 | 01LCE70AA550 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE70BR550 | Condensate | 37/vacuum | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
191 | 01LCE71AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE71BR001 | Condensate | 37/vacuum | 105 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
192 | 01LCE71AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE71BR004 | Condensate | 37 | 105 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
193 | 01LCE71AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE71BR003 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
194 | 01LCE71AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE71BR502 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
195 | 01LCE71AA551 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE71BR551 | Condensate | 37 | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
196 | 01LCE72AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE72BR001 | Condensate | 37/vacuum | 105 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
197 | 01LCE72AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCE72BR004 | Condensate | 37 | 105 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
198 | 01LCE72AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE72BR002 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
199 | 01LCE72AA504 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE72BR504 | Condensate | 37/vacuum | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  | Valve with vacuum packing
200 | 01LCE72AA505 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCE72BR505 | Condensate | 37 | 105 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
201 | 01MAL30AA701 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
202 | 01MAL30AA702 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
203 | 01MAL30AA703 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
204 | 01MAL30AA704 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
205 | 01MAL30AA707 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
206 | 01MAL30AA708 | RDST-00-MAL-MDD-EAI-11300 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
207 | 01MAL30AA709 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5 | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
208 | 01MAL31AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 100 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01MAL31BR001 | Condensate | 3.5 | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
209 | 01MAL31AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 80 mm | Swing check valve | A-216 Gr WCB | AA1RB | CL150 | BW | STD | 01MAL31BR002 | Condensate | 5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
210 | 01MAL31AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01MAL31BR002 | Condensate | 5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
211 | 01MAL31AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL31BR501 | Condensate | 3.5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
212 | 01MAL31AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL31BR502 | Condensate | 5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
213 | 01MAL31AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL31BR001 | Condensate | 3.5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
214 | 01MAL31AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL31BR002 | Condensate | 5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
215 | 01MAL32AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 100 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01MAL32BR001 | Condensate | 3.5 | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
216 | 01MAL32AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 80 mm | Swing check valve | A-216 Gr WCB | AA1RB | CL150 | BW | STD | 01MAL32BR002 | Condensate | 5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
217 | 01MAL32AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01MAL32BR002 | Condensate | 5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
218 | 01MAL32AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL32BR501 | Condensate | 3.5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
219 | 01MAL32AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL32BR502 | Condensate | 5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
220 | 01MAL32AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL32BR001 | Condensate | 3.5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
221 | 01MAL32AA702 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL32BR002 | Condensate | 5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
222 | 01MAL33AA501 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL33BR501 | Condensate | 5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
223 | 01MAL33AA551 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL33BR551 | Condensate | 5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
224 | 01MAL33AA552 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL33BR552 | Condensate | 5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
225 | 01MAL33AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL33BR001 | Condensate | 5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
226 | 01MAL41AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL41BR502 | Condensate | 3.5 | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
227 | 01MAL60AA503 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL60BR503 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
228 | 01MAL60AA701 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
229 | 01MAL60AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
230 | 01MAL60AA703 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
231 | 01MAL60AA704 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
232 | 01MAL60AA705 | RDST-00-MAL-MDD-EAI-11300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
233 | 01MAL60AA706 | RDST-00-MAL-MDD-EAI-11300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
234 | 01MAL60AA707 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
235 | 01MAL61AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 200 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | 20 | 01MAL61BR001 | Condensate | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
236 | 01MAL61AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 150 mm | Swing check valve | A-216 Gr WCB | AA1RB | CL150 | BW | STD | 01MAL61BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
237 | 01MAL61AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 150 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01MAL61BR002 | Condensate | 4/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
238 | 01MAL61AA004 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL61BR550 | Air-Water | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
239 | 01MAL61AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL61BR501 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
240 | 01MAL61AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL61BR502 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
241 | 01MAL61AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL61BR001 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
242 | 01MAL61AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL61BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
243 | 01MAL62AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 200 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | 20 | 01MAL62BR001 | Condensate | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
244 | 01MAL62AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 150 mm | Swing check valve | A-216 Gr WCB | AA1RB | CL150 | BW | STD | 01MAL62BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
245 | 01MAL62AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 150 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01MAL62BR002 | Condensate | 4/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
246 | 01MAL62AA004 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL62BR550 | Air-Water | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
247 | 01MAL62AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL62BR501 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
248 | 01MAL62AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL62BR502 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
249 | 01MAL62AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL62BR001 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
250 | 01MAL62AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL62BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
251 | 01MAL63AA501 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL63BR501 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
252 | 01MAL63AA551 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL63BR551 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
253 | 01MAL63AA552 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL63BR552 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
254 | 01MAL63AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL63BR001 | Water | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
255 | 01MAL70AA503 | RDST-00-MAL-MDD-EAI-11300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL70BR503 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
256 | 01MAL70AA701 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
257 | 01MAL70AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
258 | 01MAL70AA703 | RDST-00-MAL-MDD-EAI-11300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
259 | 01MAL70AA704 | RDST-00-MAL-MDD-EAI-11300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
260 | 01MAL70AA705 | RDST-00-MAL-MDD-EAI-11300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
261 | 01MAL70AA706 | RDST-00-MAL-MDD-EAI-11300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
262 | 01MAL70AA707 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
263 | 01MAL70AA708 | RDST-00-MAL-MDD-EAI-11300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 350 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
264 | 01MAL71AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 150 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01MAL71BR001 | Condensate | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
265 | 01MAL71AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 100 mm | Swing check valve | A-216 Gr WCB | AA1RB | CL150 | BW | STD | 01MAL71BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
266 | 01MAL71AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01MAL71BR002 | Condensate | 4/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
267 | 01MAL71AA004 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL71BR550 | Air-Water | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
268 | 01MAL71AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL71BR501 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
269 | 01MAL71AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL71BR502 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
270 | 01MAL71AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL71BR001 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
271 | 01MAL71AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL71BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
272 | 01MAL72AA001 | RDST-00-MAL-MDD-EAI-11300 | I | 150 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01MAL72BR001 | Condensate | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
273 | 01MAL72AA002 | RDST-00-MAL-MDD-EAI-11300 | I | 100 mm | Swing check valve | A-216 Gr WCB | AA1RB | CL150 | BW | STD | 01MAL72BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
274 | 01MAL72AA003 | RDST-00-MAL-MDD-EAI-11300 | I | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01MAL72BR002 | Condensate | 4/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
275 | 01MAL72AA004 | RDST-00-MAL-MDD-EAI-11300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL72BR550 | Air-Water | 3.5/vacuum | 120 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
276 | 01MAL72AA501 | RDST-00-MAL-MDD-EAI-11300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL72BR501 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
277 | 01MAL72AA502 | RDST-00-MAL-MDD-EAI-11300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL72BR502 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
278 | 01MAL72AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL72BR001 | Condensate | 3.5/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
279 | 01MAL72AA702 | RDST-00-MAL-MDD-EAI-11300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL72BR002 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
280 | 01MAL73AA501 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL73BR501 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
281 | 01MAL73AA551 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL73BR551 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
282 | 01MAL73AA552 | RDST-00-MAL-MDD-EAI-11300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAL73BR552 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
283 | 01MAL73AA701 | RDST-00-MAL-MDD-EAI-11300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01MAL73BR001 | Condensate | 4/vacuum | 120 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
284 | 01MAN10AA501 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01MAN10BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
285 | 01MAN10AA502 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01MAN10BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
286 | 01MAN10AA503 | RDST-00-LB_-MDD-EAI-10200 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01MAN10BR503 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
287 | 01MAN10AA504 | RDST-00-LB_-MDD-EAI-10200 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01MAN10BR503 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
288 | 01MAN20AA001 | RDST-00-LB_-MDD-EAI-10200 | I | 150 mm | Globe Valve | A-216 Gr WCB | AB1TB | CL300 | BW | STD | 01MAN20BR001 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
289 | 01MAN20AA002 | RDST-00-LB_-MDD-EAI-10200 | I | 150 mm | Globe valve, closed | A-216 Gr WCB | AB1TB | CL300 | BW | STD | 01LCE04BR002 | Condensate | 37/-1 | 105 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
290 | 01MAN20AA502 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAN20BR502 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
291 | 01MAN20AA503 | RDST-00-LB_-MDD-EAI-10200 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01MAN20BR503 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
292 | 01MAN20AA504 | RDST-00-LB_-MDD-EAI-10200 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01MAN20BR504 | Condensate | 37/-1 | 105 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
293 | 01QLB20AA001 | RDST-00-QLB-MDD-EAI-13300 | I | 150 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01QLB20BR002 | Steam | 18 | 343 |  |  | K | 110 mm |  | 478-00-SV-M-24300 |  | CS-HI
294 | 01QLB20AA002 | RDST-00-QLB-MDD-EAI-13300 | I | 150 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01QLB20BR002 | Steam | 18 | 343 |  |  |  | 110 mm |  | 478-00-SV-M-24300 |  | CS-HI
295 | 01QLB20AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB20BR002 | Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
296 | 01QLB20AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB20BR002 | Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
297 | 01QLB22AA001 | RDST-00-QLB-MDD-EAI-13300 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB22BR002 | Steam | 18 | 343 |  |  | K | 90 mm |  | 478-00-SV-M-24300 |  | CS-HI
298 | 01QLB22AA501 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB22BR501 | Condensate | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
299 | 01QLB22AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB22BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
300 | 01QLB22AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB22BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
301 | 01QLB22AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB22BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
302 | 01QLB22AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB22BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
303 | 01QLB30AA002 | RDST-00-QLB-MDD-EAI-13300 | E | 100 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01QLB30BR002 | Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
304 | 01QLB31AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB31BR002 | Steam | 18 | 290 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
305 | 01QLB31AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB31BR501 | Condensate | 18 | 290 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
306 | 01QLB31AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB31BR001 | Water-Steam | 18 | 290 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
307 | 01QLB31AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB31BR001 | Water-Steam | 18 | 290 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
308 | 01QLB31AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB31BR001 | Water-Steam | 18 | 290 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
309 | 01QLB31AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB31BR001 | Water-Steam | 18 | 290 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
310 | 01QLB32AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB32BR002 | Water-Steam | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
311 | 01QLB32AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB32BR501 | Condensate | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
312 | 01QLB32AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB32BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
313 | 01QLB32AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB32BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
314 | 01QLB32AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB32BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
315 | 01QLB32AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB32BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
316 | 01QLB34AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB34BR002 | Steam | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
317 | 01QLB34AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB34BR501 | Condensate | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
318 | 01QLB34AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB34BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
319 | 01QLB34AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB34BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
320 | 01QLB34AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB34BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
321 | 01QLB34AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB34BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
322 | 01QLB41AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB41BR002 | Steam | 18 | 343 |  |  | K | 90 mm |  | 478-00-SV-M-24300 |  | CS-HI
323 | 01QLB41AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB41BR501 | Condensate | 18 | 343 |  |  | K | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
324 | 01QLB41AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB41BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
325 | 01QLB41AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB41BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
326 | 01QLB41AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB41BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
327 | 01QLB41AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB41BR001 | Water-Steam | 18 | 343 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
328 | 01QLB50AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 100 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01QLB50BR004 | Steam | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
329 | 01QLB50AA002 | RDST-00-QLB-MDD-EAI-13300 | E | 100 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01QLB50BR004 | Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
330 | 01QLB50AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB50BR002 | Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
331 | 01QLB50AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB50BR002 | Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
332 | 01QLB51AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR002 | Steam | 196 | 365 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
333 | 01QLB51AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR501 | Condensate | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
334 | 01QLB51AA502 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR501 | Condensate | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
335 | 01QLB51AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
336 | 01QLB51AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
337 | 01QLB51AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
338 | 01QLB51AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
339 | 01QLB51AA705 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
340 | 01QLB51AA706 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
341 | 01QLB51AA707 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
342 | 01QLB51AA708 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01QLB51BR001 | Water-Steam | 196 | 365 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
343 | 01QLB52AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB52BR002 | Steam | 18 | 223 |  |  | K | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
344 | 01QLB52AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB52BR501 | Condensate | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
345 | 01QLB52AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB52BR001 | Water-Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
346 | 01QLB52AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB52BR001 | Water-Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
347 | 01QLB52AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB52BR001 | Water-Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
348 | 01QLB52AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB52BR001 | Water-Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
349 | 01QLB54AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 15 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | XS | 01QLB54BR001 | Steam | 196 | 365 |  |  | K | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
350 | 01QLB54AA101 | RDST-00-QLB-MDD-EAI-13300 | E | 15 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | XS | 01QLB54BR101 | Steam | 196 | 365 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
351 | 01QLB55AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB55BR001 | Steam | 18 | 223 |  |  | K | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
352 | 01QLB55AA101 | RDST-00-QLB-MDD-EAI-13300 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01QLB55BR101 | Steam | 18 | 223 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
353 | 01QLB60AA705 | RDST-00-QLB-MDD-EAI-13300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB60BR002 | Steam | 16 | 343 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
354 | 01QLB60AA708 | RDST-00-QLB-MDD-EAI-13300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB60BR002 | Steam | 16 | 343 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
355 | 01QLB64AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB64BR002 | Steam | 16 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
356 | 01QLB64AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB64BR501 | Condensate | 16 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
357 | 01QLB64AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB64BR001 | Water-Steam | 16 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
358 | 01QLB64AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB64BR001 | Water-Steam | 16 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
359 | 01QLB64AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB64BR001 | Water-Steam | 16 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
360 | 01QLB64AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB64BR001 | Water-Steam | 16 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
361 | 01QLB70AA701 | RDST-00-QLB-MDD-EAI-13300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB70BR001 | Steam | 18 | 343 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
362 | 01QLB71AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB71BR002 | Water-Steam | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
363 | 01QLB71AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB71BR501 | Condensate | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
364 | 01QLB71AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB71BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
365 | 01QLB71AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB71BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
366 | 01QLB71AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB71BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
367 | 01QLB71AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB71BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
368 | 01QLB72AA001 | RDST-00-QLB-MDD-EAI-13300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB72BR002 | Water-Steam | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
369 | 01QLB72AA501 | RDST-00-QLB-MDD-EAI-13300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01QLB72BR501 | Condensate | 18 | 343 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
370 | 01QLB72AA701 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB72BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
371 | 01QLB72AA702 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB72BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
372 | 01QLB72AA703 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB72BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
373 | 01QLB72AA704 | RDST-00-QLB-MDD-EAI-13300 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01QLB72BR001 | Water-Steam | 18 | 343 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
374 | 01GMA10AA001 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR002 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
375 | 01GMA10AA002 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR003 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
376 | 01GMA10AA003 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR004 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
377 | 01GMA10AA004 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR012 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
378 | 01GMA10AA005 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR014 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
379 | 01GMA10AA006 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR016 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
380 | 01GMA10AA007 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR026 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
381 | 01GMA10AA008 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR005 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
382 | 01GMA10AA009 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR009 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
383 | 01GMA10AA010 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Gate valve, closed | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01GMA10BR017 | Oily Water | 0.49 | 100 |  |  | E |  |  | 478-00-SV-M-24300 |  | CS-LU-ImR | 6032
384 | 01GMA15AA001 | RDST-00-GM_-MDD-EAI-14500 | I | 80 mm | Swing check valve | A-216 Gr WCB | AA1RF | CL150 | FL | STD | 01GMA15BR001 | Oily Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
385 | 01GMA15AA002 | RDST-00-GM_-MDD-EAI-14500 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01GMA15BR001 | Oily Water | 3.5 | 60 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
386 | 01GMA15AA003 | RDST-00-GM_-MDD-EAI-14500 | I | 80 mm | Swing check valve | A-216 Gr WCB | AA1RF | CL150 | FL | STD | 01GMA15BR002 | Oily Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
387 | 01GMA15AA004 | RDST-00-GM_-MDD-EAI-14500 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01GMA15BR002 | Oily Water | 3.5 | 60 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
388 | 01GMA15AA501 | RDST-00-GM_-MDD-EAI-14500 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GMA15BR501 | Oily Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
389 | 01GMA15AA502 | RDST-00-GM_-MDD-EAI-14500 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GMA15BR502 | Oily Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
390 | 01GMA15AA701 | RDST-00-GM_-MDD-EAI-14500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GMA15BR001 | Oily Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
391 | 01GMA15AA702 | RDST-00-GM_-MDD-EAI-14500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GMA15BR002 | Oily Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
392 | 01GMB10AA002 | RDST-00-GM_-MDD-EAI-14500 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01GMB10BR020 | Waste Water | 3.5 | 60 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
393 | 01GMB10AA003 | RDST-00-GM_-MDD-EAI-14500 | E | 100 mm | Swing check valve | A-216 Gr WCB | AA1RF | CL150 | FL | STD | 01GMB10BR021 | Waste Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
394 | 01GMB10AA004 | RDST-00-GM_-MDD-EAI-14500 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01GMB10BR021 | Waste Water | 3.5 | 60 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
395 | 01GMB10AA005 | RDST-00-GM_-MDD-EAI-14500 | E | 100 mm | Swing check valve | A-216 Gr WCB | AA1RF | CL150 | FL | STD | 01GMB10BR020 | Waste Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
396 | 01GMB10AA501 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GMB10BR501 | Waste Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
397 | 01GMB10AA502 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GMB10BR502 | Waste Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
398 | 01GMB10AA701 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GMB10BR020 | Waste Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
399 | 01GMB10AA702 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GMB10BR021 | Waste Water | 3.5 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
400 | 01GMB20AA001 | RDST-00-GM_-MDD-EAI-14500 | E | 65 mm | Swing check valve | A-216 Gr WCB | AA1RF | CL150 | FL | STD | 01GMB20BR003 | Waste Water | 4 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
401 | 01GMB20AA002 | RDST-00-GM_-MDD-EAI-14500 | E | 65 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01GMB20BR003 | Waste Water | 4 | 60 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
402 | 01GMB20AA003 | RDST-00-GM_-MDD-EAI-14500 | E | 65 mm | Swing check valve | A-216 Gr WCB | AA1RF | CL150 | FL | STD | 01GMB20BR004 | Waste Water | 4 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
403 | 01GMB20AA004 | RDST-00-GM_-MDD-EAI-14500 | E | 65 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01GMB20BR004 | Waste Water | 4 | 60 |  |  | K |  |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
404 | 01GMB20AA501 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GMB20BR501 | Waste Water | 4 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
405 | 01GMB20AA502 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01GMB20BR502 | Waste Water | 4 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
406 | 01GMB20AA701 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GMB20BR003 | Waste Water | 4 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
407 | 01GMB20AA702 | RDST-00-GM_-MDD-EAI-14500 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01GMB20BR004 | Waste Water | 4 | 60 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
408 | 01LAA50AA003 | RDST-00-LA_-MDD-EAI-10300 | E | 150 mm | Gate valve | A-216 Gr WCB | AB1CF | CL300 | FL | STD | 01LAA50BR901 | Air-Steam | 18/vacuum | 205 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing | 配供螺栓、螺母、垫片、密封垫
409 | 01LAA50AA004 | RDST-00-LA_-MDD-EAI-10300 | E | 150 mm | Gate valve | A-216 Gr WCB | AB1CF | CL300 | FL | STD | 01LAA50BR906 | Air-Steam | 18/vacuum | 205 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing | 配供螺栓、螺母、垫片、密封垫
410 | 01LAA50AA501 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR502 | Feedwater | 18/vacuum | 205 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
411 | 01LAA50AA502 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR503 | Feedwater | 18/vacuum | 205 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
412 | 01LAA50AA503 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR504 | Nitrogen | 18/vacuum | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
413 | 01LAA50AA703 | RDST-00-LA_-MDD-EAI-10300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
414 | 01LAA50AA704 | RDST-00-LA_-MDD-EAI-10300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
415 | 01LAA50AA705 | RDST-00-LA_-MDD-EAI-10300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
416 | 01LAA50AA706 | RDST-00-LA_-MDD-EAI-10300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
417 | 01LAA50AA707 | RDST-00-LA_-MDD-EAI-10300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
418 | 01LAA50AA708 | RDST-00-LA_-MDD-EAI-10300 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
419 | 01LAA50AA709 | RDST-00-LA_-MDD-EAI-10300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18/vacuum | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
420 | 01LAA50AA710 | RDST-00-LA_-MDD-EAI-10300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18/vacuum | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
421 | 01LAA50AA711 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18/vacuum | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
422 | 01LAA50AA712 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18/vacuum | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
423 | 01LAA50AA713 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18/vacuum | 205 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
424 | 01LAA50AA714 | RDST-00-LA_-MDD-EAI-10300 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR004 | Feedwater | 18/vacuum | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
425 | 01LAA50AA716 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAA50BR001 | Feedwater | 18 | 205 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
426 | 01LAB03AA001 | RDST-00-LA_-MDD-EAI-10300 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LAB03BR001 | Feedwater | 18 | 205 |  |  | K | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
427 | 01LAB03AA002 | RDST-00-LA_-MDD-EAI-10300 | E | 200 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LAB03BR002 | Feedwater | 18/vacuum | 205 |  |  | K | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
428 | 01LAB03AA501 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB03BR501 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
429 | 01LAB03AA502 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB03BR501 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
430 | 01LAB03AA503 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB03BR502 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
431 | 01LAB03AA504 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB03BR502 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
432 | 01LAB10AA001 | RDST-00-LA_-MDD-EAI-10300 | I | 250 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LAB10BR001 | Feedwater | 18 | 205 |  |  | RK | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
433 | 01LAB10AA003 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR003 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
434 | 01LAB10AA101 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR002 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
435 | 01LAB10AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR501 | Air-Water | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
436 | 01LAB10AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR502 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
437 | 01LAB10AA703 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR001 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
438 | 01LAB10AA704 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR001 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
439 | 01LAB10AA705 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR001 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
440 | 01LAB10AA706 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB10BR001 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
441 | 01LAB11AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB11BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
442 | 01LAB11AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB11BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
443 | 01LAB11AA701 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB11BR001 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
444 | 01LAB11AA702 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB11BR001 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
445 | 01LAB11AA707 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
446 | 01LAB11AA708 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
447 | 01LAB11AA709 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
448 | 01LAB11AA710 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
449 | 01LAB11AA711 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
450 | 01LAB11AA712 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
451 | 01LAB11AA713 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
452 | 01LAB11AA714 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
453 | 01LAB12AA501 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB12BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
454 | 01LAB12AA502 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB12BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
455 | 01LAB12AA503 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB12BR502 | Air-Water | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
456 | 01LAB12AA504 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB12BR502 | Air-Water | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
457 | 01LAB20AA001 | RDST-00-LA_-MDD-EAI-10300 | I | 250 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LAB20BR001 | Feedwater | 18 | 205 |  |  | RK | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
458 | 01LAB20AA003 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB20BR003 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
459 | 01LAB20AA101 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB20BR002 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
460 | 01LAB20AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB20BR501 | Air-Water | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
461 | 01LAB20AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAB20BR502 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
462 | 01LAB20AA703 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB20BR001 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
463 | 01LAB20AA704 | RDST-00-LA_-MDD-EAI-10300 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
464 | 01LAB20AA705 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAB20BR001 | Feedwater | 18 | 205 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
465 | 01LAB20AA706 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Feedwater | 18 | 205 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
466 | 01LAB21AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB21BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
467 | 01LAB21AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB21BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
468 | 01LAB21AA701 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB21BR001 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
469 | 01LAB21AA702 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB21BR001 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
470 | 01LAB21AA707 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
471 | 01LAB21AA708 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
472 | 01LAB21AA709 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
473 | 01LAB21AA710 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
474 | 01LAB21AA711 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
475 | 01LAB21AA712 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
476 | 01LAB21AA713 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
477 | 01LAB21AA714 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 |  | Feedwater | 275 | 211 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
478 | 01LAB22AA501 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB22BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
479 | 01LAB22AA502 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB22BR501 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
480 | 01LAB22AA503 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB22BR502 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
481 | 01LAB22AA504 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB22BR502 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
482 | 01LAB40AA705 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB40BR001 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
483 | 01LAB40AA706 | RDST-00-LA_-MDD-EAI-10300 | E | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB40BR001 | Feedwater | 275 | 211 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
484 | 01LAB42AA101 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR005 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
485 | 01LAB42AA102 | RDST-00-LA_-MDD-EAI-10300 | I | 15 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR005 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
486 | 01LAB42AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
487 | 01LAB42AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
488 | 01LAB42AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
489 | 01LAB42AA503 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR503 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
490 | 01LAB42AA504 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR503 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
491 | 01LAB42AA505 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR502 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
492 | 01LAB42AA506 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR502 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
493 | 01LAB42AA509 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR505 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
494 | 01LAB42AA510 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR505 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
495 | 01LAB42AA701 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR001 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
496 | 01LAB42AA702 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR001 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
497 | 01LAB42AA703 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR001 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
498 | 01LAB42AA704 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR001 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
499 | 01LAB42AA705 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
500 | 01LAB42AA706 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
501 | 01LAB42AA707 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
502 | 01LAB42AA708 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
503 | 01LAB42AA709 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
504 | 01LAB42AA710 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
505 | 01LAB42AA711 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
506 | 01LAB42AA712 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
507 | 01LAB42AA713 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
508 | 01LAB42AA714 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
509 | 01LAB42AA715 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
510 | 01LAB42AA716 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
511 | 01LAB42AA717 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
512 | 01LAB42AA718 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB42BR002 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
513 | 01LAB43AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR501 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
514 | 01LAB43AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR501 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
515 | 01LAB43AA503 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR504 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
516 | 01LAB43AA504 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR504 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
517 | 01LAB43AA505 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR502 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
518 | 01LAB43AA506 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR502 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
519 | 01LAB43AA507 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR503 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
520 | 01LAB43AA508 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR503 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
521 | 01LAB43AA701 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR001 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
522 | 01LAB43AA702 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR001 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
523 | 01LAB43AA703 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR001 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
524 | 01LAB43AA704 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR001 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
525 | 01LAB43AA705 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR002 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
526 | 01LAB43AA706 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR002 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
527 | 01LAB43AA707 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR002 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
528 | 01LAB43AA708 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR002 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
529 | 01LAB43AA709 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR002 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
530 | 01LAB43AA710 | RDST-00-LA_-MDD-EAI-10300 | I | 20 mm | Globe Valve | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB43BR002 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
531 | 01LAB60AA501 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB60BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
532 | 01LAB60AA502 | RDST-00-LA_-MDD-EAI-10300 | E | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAB60BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
533 | 01LAC10AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 40 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAC10BR501 | Feedwater | 0.49 | 205 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
534 | 01LAC20AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 40 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAC20BR501 | Feedwater | 0.49 | 205 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI
535 | 01LAD50AA505 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR505 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
536 | 01LAD50AA506 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR502 | Condensate | 77 | 295 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
537 | 01LAD50AA507 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR507 | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
538 | 01LAD50AA513 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR502 | Condensate | 77 | 295 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
539 | 01LAD50AA515 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR505 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
540 | 01LAD50AA517 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR507 | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
541 | 01LAD50AA705 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
542 | 01LAD50AA706 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
543 | 01LAD50AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
544 | 01LAD50AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
545 | 01LAD50AA709 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
546 | 01LAD50AA710 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
547 | 01LAD50AA713 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
548 | 01LAD50AA714 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
549 | 01LAD50AA715 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
550 | 01LAD50AA716 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
551 | 01LAD50AA717 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
552 | 01LAD50AA718 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
553 | 01LAD50AA719 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
554 | 01LAD50AA720 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
555 | 01LAD50AA721 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
556 | 01LAD50AA722 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD50BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
557 | 01LAD60AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR501 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
558 | 01LAD60AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR501 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
559 | 01LAD60AA503 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR502 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
560 | 01LAD60AA503 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR503 | Condensate | 28/vacuum | 231 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
561 | 01LAD60AA504 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR502 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
562 | 01LAD60AA505 | RDST-00-LA_-MDD-EAI-10500 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR505 | Water-Steam | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
563 | 01LAD60AA507 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR509 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
564 | 01LAD60AA507 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR507 | Water-Steam | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
565 | 01LAD60AA508 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR509 | Feedwater | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
566 | 01LAD60AA509 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR510 | Nitrogen | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
567 | 01LAD60AA510 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD60BR510 | Nitrogen | 275 | 250 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
568 | 01LAD60AA703 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
569 | 01LAD60AA704 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
570 | 01LAD60AA705 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
571 | 01LAD60AA706 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
572 | 01LAD60AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
573 | 01LAD60AA708 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
574 | 01LAD60AA709 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
575 | 01LAD60AA710 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
576 | 01LAD60AA711 | RDST-00-LA_-MDD-EAI-10500 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LAD60BR002 | Water-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
577 | 01LAD70AA501 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
578 | 01LAD70AA502 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR501 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
579 | 01LAD70AA503 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR502 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
580 | 01LAD70AA503 | RDST-00-LA_-MDD-EAI-10500 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR503 | Water-Steam | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
581 | 01LAD70AA504 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR502 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
582 | 01LAD70AA505 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH70BR505 | Condensate | 44/vacuum | 257 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
583 | 01LAD70AA506 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR504 | Water-Steam | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
584 | 01LAD70AA507 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR506 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
585 | 01LAD70AA508 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR506 | Feedwater | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
586 | 01LAD70AA509 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR507 | Nitrogen | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
587 | 01LAD70AA510 | RDST-00-LA_-MDD-EAI-10300 | I | 25 mm | Globe valve, closed | A-105 | AG1TS | CL2500 | SW | 160 | 01LAD70BR507 | Nitrogen | 275 | 276 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI
588 | 01LAD70AA701 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR002 | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
589 | 01LAD70AA702 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR002 | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
590 | 01LAD70AA703 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR002 | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
591 | 01LAD70AA704 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR002 | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
592 | 01LAD70AA705 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR002 | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
593 | 01LAD70AA706 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD70BR002 | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
594 | 01LAD70AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
595 | 01LAD70AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
596 | 01LAD80AA505 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR505 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
597 | 01LAD80AA506 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR502 | Condensate | 77 | 295 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
598 | 01LAD80AA507 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR507 | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
599 | 01LAD80AA513 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR502 | Condensate | 77 | 295 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
600 | 01LAD80AA515 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR505 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
601 | 01LAD80AA517 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR507 | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
602 | 01LAD80AA705 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
603 | 01LAD80AA706 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
604 | 01LAD80AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
605 | 01LAD80AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
606 | 01LAD80AA709 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
607 | 01LAD80AA710 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
608 | 01LAD80AA713 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
609 | 01LAD80AA714 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
610 | 01LAD80AA715 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
611 | 01LAD80AA716 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
612 | 01LAD80AA717 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
613 | 01LAD80AA718 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
614 | 01LAD80AA719 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
615 | 01LAD80AA720 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS |  | Water-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
616 | 01LAD80AA721 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
617 | 01LAD80AA722 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LAD80BR002 | Water-Steam | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
618 | 01LCC10AA503 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR503 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
619 | 01LCC10AA505 | RDST-00-LA_-MDD-EAI-10500 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR505 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
620 | 01LCC10AA507 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR507 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
621 | 01LCC10AA703 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
622 | 01LCC10AA704 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
623 | 01LCC10AA705 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
624 | 01LCC10AA706 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
625 | 01LCC10AA707 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
626 | 01LCC10AA708 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
627 | 01LCC10AA709 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
628 | 01LCC10AA710 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
629 | 01LCC10AA711 | RDST-00-LA_-MDD-EAI-10500 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC10BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
630 | 01LCC20AA503 | RDST-00-LA_-MDD-EAI-10500 | I | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR503 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
631 | 01LCC20AA505 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR505 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
632 | 01LCC20AA507 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR507 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
633 | 01LCC20AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
634 | 01LCC20AA702 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
635 | 01LCC20AA703 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
636 | 01LCC20AA704 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
637 | 01LCC20AA705 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
638 | 01LCC20AA706 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
639 | 01LCC20AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
640 | 01LCC20AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
641 | 01LCC20AA711 | RDST-00-LA_-MDD-EAI-10500 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC20BR002 | Water-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
642 | 01LCC30AA503 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR503 | Condensate | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
643 | 01LCC30AA505 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR505 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
644 | 01LCC30AA507 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR507 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
645 | 01LCC30AA703 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
646 | 01LCC30AA704 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
647 | 01LCC30AA705 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
648 | 01LCC30AA706 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
649 | 01LCC30AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
650 | 01LCC30AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
651 | 01LCC30AA709 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
652 | 01LCC30AA710 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
653 | 01LCC30AA711 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC30BR002 | Water-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
654 | 01LCC40AA503 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR503 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
655 | 01LCC40AA504 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR504 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
656 | 01LCC40AA505 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR505 | Condensate | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
657 | 01LCC40AA701 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
658 | 01LCC40AA702 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
659 | 01LCC40AA703 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
660 | 01LCC40AA704 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
661 | 01LCC40AA705 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
662 | 01LCC40AA706 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
663 | 01LCC40AA707 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
664 | 01LCC40AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
665 | 01LCC40AA711 | RDST-00-LA_-MDD-EAI-10500 | E | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCC40BR002 | Water-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
666 | 01LCH42AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LCH42BR003 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
667 | 01LCH42AA002 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LCH42BR001 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
668 | 01LCH42AA003 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH42BR002 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
669 | 01LCH42AA004 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH42BR004 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
670 | 01LCH50AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 100 mm | Gate valve | A-216 Gr WCB | AD1CB | CL600 | BW | XS | 01LCH50BR001 | Condensate | 77 | 295 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
671 | 01LCH50AA003 | RDST-00-LA_-MDD-EAI-10500 | E | 100 mm | Swing check valve | A-216 Gr WCB | AD1RB | CL600 | BW | XS | 01LCH50BR001 | Condensate | 77 | 295 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
672 | 01LCH50AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH50BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
673 | 01LCH50AA502 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH50BR502 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
674 | 01LCH50AA503 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH50BR502 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
675 | 01LCH50AA511 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH50BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
676 | 01LCH50AA701 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH50BR001 | Condensate | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
677 | 01LCH50AA702 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH50BR001 | Condensate | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
678 | 01LCH51AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 100 mm | Gate valve | A-216 Gr WCB | AD1CB | CL600 | BW | XS | 01LCH51BR001 | Condensate | 77 | 295 |  |  | K | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
679 | 01LCH51AA501 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH51BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
680 | 01LCH51AA511 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH51BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
681 | 01LCH52AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LCH52BR003 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
682 | 01LCH52AA002 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LCH52BR001 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
683 | 01LCH52AA003 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH52BR002 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
684 | 01LCH52AA004 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH52BR004 | Air-Steam | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
685 | 01LCH60AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 150 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCH60BR001 | Condensate | 28/vacuum | 231 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
686 | 01LCH60AA004 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCH60BR001 | Condensate | 28/vacuum | 231 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
687 | 01LCH60AA501 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCH60BR501 | Condensate | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
688 | 01LCH60AA502 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCH60BR502 | Condensate | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
689 | 01LCH60AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCH60BR001 | Condensate | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
690 | 01LCH60AA702 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCH60BR001 | Condensate | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
691 | 01LCH61AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCH61BR001 | Condensate | 28/vacuum | 231 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
692 | 01LCH61AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCH61BR501 | Condensate | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
693 | 01LCH62AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCH62BR004 | Air-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
694 | 01LCH62AA002 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCH62BR001 | Air-Steam | 28/vacuum | 231 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
695 | 01LCH62AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCH62BR003 | Air-Steam | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
696 | 01LCH62AA004 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCH62BR002 | Air-Steam | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
697 | 01LCH62AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01LCH62BR501 | Nitrogen | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
698 | 01LCH65AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCH65BR001 | Condensate | 28/vacuum | 231 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
699 | 01LCH70AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Gate valve | A-216 Gr WCB | AD1CB | CL600 | BW | XS | 01LCH70BR001 | Condensate | 44/vacuum | 257 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
700 | 01LCH70AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH70BR501 | Condensate | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
701 | 01LCH70AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH70BR001 | Condensate | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
702 | 01LCH71AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Gate valve | A-216 Gr WCB | AD1CB | CL600 | BW | XS | 01LCH71BR001 | Condensate | 44/vacuum | 257 |  |  | K | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
703 | 01LCH71AA502 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH71BR501 | Condensate | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
704 | 01LCH72AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LCH72BR003 | Air-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
705 | 01LCH72AA002 | RDST-00-LA_-MDD-EAI-10500 | E | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | XS | 01LCH72BR001 | Air-Steam | 44/vacuum | 257 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
706 | 01LCH72AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH72BR002 | Air-Steam | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
707 | 01LCH72AA004 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH72BR004 | Air-Steam | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
708 | 01LCH72AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | 160 | 01LCH72BR501 | Nitrogen | 44/vacuum | 257 |  |  |  | 50 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
709 | 01LCH80AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 100 mm | Gate valve | A-216 Gr WCB | AD1CB | CL600 | BW | XS | 01LCH80BR001 | Condensate | 77 | 295 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
710 | 01LCH80AA003 | RDST-00-LA_-MDD-EAI-10500 | E | 100 mm | Swing check valve | A-216 Gr WCB | AD1RB | CL600 | BW | XS | 01LCH80BR001 | Condensate | 77 | 295 |  |  |  | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
711 | 01LCH80AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH80BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
712 | 01LCH80AA502 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH80BR502 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
713 | 01LCH80AA503 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH80BR502 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
714 | 01LCH80AA511 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH80BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
715 | 01LCH80AA701 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH80BR001 | Condensate | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
716 | 01LCH80AA702 | RDST-00-LA_-MDD-EAI-10500 | E | 20 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH80BR001 | Condensate | 77 | 295 |  |  |  | 60 mm |  | 478-00-SV-M-24300 |  | CS-HI
717 | 01LCH81AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 100 mm | Gate valve | A-216 Gr WCB | AD1CB | CL600 | BW | XS | 01LCH81BR001 | Condensate | 77 | 295 |  |  | K | 80 mm |  | 478-00-SV-M-24300 |  | CS-HI
718 | 01LCH81AA501 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH81BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
719 | 01LCH81AA502 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCH81BR501 | Condensate | 77 | 295 |  |  |  | 70 mm |  | 478-00-SV-M-24300 |  | CS-HI
720 | 01LCJ10AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 80 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ10BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
721 | 01LCJ10AA501 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ10BR501 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
722 | 01LCJ10AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ10BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
723 | 01LCJ11AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ11BR001 | Condensate | 3.5/vacuum | 148 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
724 | 01LCJ11AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ11BR501 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
725 | 01LCJ12AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ12BR003 | Air-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
726 | 01LCJ12AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ12BR001 | Air-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
727 | 01LCJ12AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ12BR002 | Air-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
728 | 01LCJ12AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCJ12BR501 | Nitrogen | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
729 | 01LCJ16AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ16BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
730 | 01LCJ16AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ16BR002 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
731 | 01LCJ20AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ20BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
732 | 01LCJ21AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ21BR001 | Condensate | 3.5/vacuum | 148 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
733 | 01LCJ21AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ21BR501 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
734 | 01LCJ22AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ22BR003 | Air-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
735 | 01LCJ22AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ22BR001 | Air-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
736 | 01LCJ22AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ22BR002 | Air-Steam | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
737 | 01LCJ22AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCJ22BR501 | Nitrogen | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
738 | 01LCJ23AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ23BR001 | Condensate | 3.5/vacuum | 148 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
739 | 01LCJ23AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCJ23BR002 | Condensate | 37/vacuum | 148 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
740 | 01LCJ23AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCJ23BR002 | Condensate | 37/vacuum | 148 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
741 | 01LCJ23AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ23BR501 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
742 | 01LCJ23AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ23BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
743 | 01LCJ23AA702 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ23BR002 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
744 | 01LCJ23AA703 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ23BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
745 | 01LCJ23AA713 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ23BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
746 | 01LCJ24AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 150 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ24BR001 | Condensate | 3.5/vacuum | 148 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
747 | 01LCJ24AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCJ24BR002 | Condensate | 37/vacuum | 148 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
748 | 01LCJ24AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCJ24BR002 | Condensate | 37/vacuum | 148 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
749 | 01LCJ24AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ24BR501 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
750 | 01LCJ24AA701 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ24BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
751 | 01LCJ24AA702 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ24BR002 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
752 | 01LCJ24AA703 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ24BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
753 | 01LCJ24AA713 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ24BR001 | Condensate | 3.5/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
754 | 01LCJ25AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCJ25BR001 | Condensate | 37/vacuum | 148 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
755 | 01LCJ25AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Gate valve | A-216 Gr WCB | AB1CB | CL300 | BW | STD | 01LCJ25BR001 | Condensate | 37/vacuum | 148 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
756 | 01LCJ25AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 80 mm | Swing check valve | A-216 Gr WCB | AB1RB | CL300 | BW | STD | 01LCJ25BR001 | Condensate | 37/vacuum | 148 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI
757 | 01LCJ25AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ25BR501 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
758 | 01LCJ25AA502 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ25BR502 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
759 | 01LCJ25AA702 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ25BR001 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
760 | 01LCJ25AA708 | RDST-00-LA_-MDD-EAI-10500 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Condensate | 44/vacuum | 257 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
761 | 01LCJ25AA709 | RDST-00-LA_-MDD-EAI-10500 | E | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Condensate | 44/vacuum | 257 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
762 | 01LCJ25AA710 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
763 | 01LCJ25AA711 | RDST-00-LA_-MDD-EAI-10500 | I | 15 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD |  | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
764 | 01LCJ26AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ26BR003 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
765 | 01LCJ27AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ27BR001 | Condensate | 37/vacuum | 148 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
766 | 01LCJ27AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 40 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ27BR004 | Condensate | 37/vacuum | 148 |  |  | K | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
767 | 01LCJ27AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 40 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ27BR002 | Condensate | 37/vacuum | 148 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
768 | 01LCJ30AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 100 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ30BR001 | Condensate | 6/vacuum | 152 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
769 | 01LCJ30AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ30BR501 | Condensate | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
770 | 01LCJ30AA701 | RDST-00-LA_-MDD-EAI-10500 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ30BR001 | Condensate | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
771 | 01LCJ31AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 150 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ31BR001 | Condensate | 6/vacuum | 152 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
772 | 01LCJ31AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ31BR501 | Condensate | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
773 | 01LCJ32AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ32BR003 | Air-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
774 | 01LCJ32AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ32BR001 | Air-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
775 | 01LCJ32AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ32BR002 | Air-Steam | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
776 | 01LCJ32AA501 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCJ32BR501 | Nitrogen | 6/vacuum | 152 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
777 | 01LCJ40AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 80 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ40BR001 | Condensate | 11/vacuum | 180 |  |  |  | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
778 | 01LCJ40AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ40BR501 | Condensate | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
779 | 01LCJ40AA701 | RDST-00-LA_-MDD-EAI-10500 | E | 15 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ40BR001 | Condensate | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
780 | 01LCJ41AA001 | RDST-00-LA_-MDD-EAI-10500 | E | 100 mm | Gate valve | A-216 Gr WCB | AA1CB | CL150 | BW | STD | 01LCJ41BR001 | Condensate | 11/vacuum | 180 |  |  | K | 40 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
781 | 01LCJ41AA501 | RDST-00-LA_-MDD-EAI-10500 | I | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ41BR501 | Condensate | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
782 | 01LCJ42AA001 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ42BR003 | Air-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
783 | 01LCJ42AA002 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01LCJ42BR001 | Air-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
784 | 01LCJ42AA003 | RDST-00-LA_-MDD-EAI-10500 | I | 50 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | STD | 01LCJ42BR002 | Air-Steam | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
785 | 01LCJ42AA501 | RDST-00-LA_-MDD-EAI-10500 | E | 25 mm | Globe valve, closed | A-105 | AD1TS | CL600 | SW | XS | 01LCJ42BR501 | Nitrogen | 11/vacuum | 180 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-HI |  |  |  | Valve with vacuum packing
786 | 01PGB46AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 200 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB46BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
787 | 01PGB44AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB44BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
788 | 01PGB42AA001 | RDST-00-PG_-MDD-EAI-12200 | I | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB42BR002 | DWater/P.Glycol | 8 | 65 |  |  | M |  |  | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
789 | 01PGB42AA002 | RDST-00-PG_-MDD-EAI-12200 | I | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | 40S | 01PGB42BR003 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
790 | 01PGB53AA001 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | 40S | 01PGB53BR001 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
791 | 01PGB53AA002 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | 40S | 01PGB53BR002 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
792 | 01PGB53AA003 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | 40S | 01PGB53BR003 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
793 | 01PGB53AA004 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | 40S | 01PGB53BR004 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24300 |  | CS-LU-IC3 | 6032
794 | 01PGB41AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB41BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
795 | 01PGB41AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 80 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB41BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
796 | 01PGB51AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 100mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB51BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
797 | 01PGB51AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB51BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
798 | 01PGB71AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB71BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
799 | 01PGB71AA003 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB71BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
800 | 01PGB71AA004 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB71BR004 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
801 | 01PGB71AA005 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB71BR005 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
802 | 01PGB71AA006 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB71BR006 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
803 | 01PGB71AA007 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB71BR007 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
804 | 01PGB71AA008 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB71BR008 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
805 | 01PGB71AA009 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB71BR009 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
806 | 01PGB72AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB72BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
807 | 01PGB72AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB72BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
808 | 01PGB72AA003 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB72BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
809 | 01PGB56AA007 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB56BR012 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
810 | 01PGB56AA008 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB56BR013 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
811 | 01PGB57AA007 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB57BR012 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
812 | 01PGB57AA008 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB57BR013 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
813 | 01PGB48AA005 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB48BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
814 | 01PGB48AA006 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Globe Valve | A-105 | AD1TS | CL600 | SW | STD | 01PGB48BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
815 | 01PGB58AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 150 mm | Globe Valve | A-216 Gr WCB | AA1TB | CL150 | BW | STD | 01PGB58BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24300 |  | CS-LU-WC4 | 6032
816 | 01GMB10AA001 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | SDR 17 | 01GMB10BR002 | Waste Water | 0.49 | 46,5 |  |  | E |  |  | 478-00-SV-M-24400 |  | CS-LU-ImR |  |  |  |  | 配供螺栓、螺母、垫片、密封垫
817 | 01GMB10AA006 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | SDR 17 | 01GMB10BR008 | Waste Water | 0.49 | 46,5 |  |  | K |  |  | 478-00-SV-M-24400 |  | CS-LU-ImR |  |  |  |  | 配供螺栓、螺母、垫片、密封垫
818 | 01GMB25AA001 | RDST-00-GM_-MDD-EAI-14500 | ENT | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | SDR 17 | 01GMB25BR001 | Waste Water | 0.49 | 46,5 |  |  | E |  |  | 478-00-SV-M-24400 |  | CS-LU-ImR |  |  |  |  | 配供螺栓、螺母、垫片、密封垫
819 | 01GMB40AA001 | RDST-00-GM_-MDD-EAI-14500 | ENT | 150 mm | Butterfly valve | A-536 Gr 60-40-18 | AM6MW | PN16 | WL | SDR 7,4 | 01GMB40BR001 | Waste Water | 0.49 | 46,5 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-ImR |  |  |  |  | 配供螺栓、螺母、垫片、密封垫
820 | 01GMB40AA002 | RDST-00-GM_-MDD-EAI-14500 | ENT | 150 mm | Butterfly valve, closed | A-536 Gr 60-40-18 | AM6MW | PN16 | WL | SDR 7,4 | 01GMB40BR002 | Waste Water | 0.49 | 46,5 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-ImR |  |  |  |  | 配供螺栓、螺母、垫片、密封垫
821 | 01MAW50AA001 | RDST-00-MAW-MDD-EAI-11200 | I | 65 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01MAW50BR001 | Air-Steam | 0.49/vacuum | 300 |  |  | M | 80 mm |  | 478-00-SV-M-24400 |  | CS-HI |  |  |  | Valve with vacuum packing | 配供螺栓、螺母、垫片、密封垫
822 | 01MAW60AA001 | RDST-00-MAW-MDD-EAI-11200 | I | 150 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01MAW60BR001 | Air-Steam | 0.49/vacuum | 350 |  |  | M | 70 mm |  | 478-00-SV-M-24400 |  | CS-HI |  |  |  | Valve with vacuum packing | 配供螺栓、螺母、垫片、密封垫
823 | 01MAW61AA001 | RDST-00-MAW-MDD-EAI-11200 | I | 65 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01MAW61BR002 | Air-Steam | 0.49/vacuum | 300 |  |  | M | 80 mm |  | 478-00-SV-M-24400 |  | CS-HI |  |  |  | Valve with vacuum packing | 配供螺栓、螺母、垫片、密封垫
824 | 01MAW66AA001 | RDST-00-MAW-MDD-EAI-11200 | I | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01MAW66BR002 | Air-Steam | 0.49/vacuum | 200 |  |  | M | 40 mm |  | 478-00-SV-M-24400 |  | CS-HI |  |  |  | Valve with vacuum packing | 配供螺栓、螺母、垫片、密封垫
825 | 01PGA44AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA44BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
826 | 01PGA46AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 200 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | 20 | 01PGA46BR001 | Air-DWater/PG | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
827 | 01PGE30AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGE30BR001 | Air-DWater/PG | 8 | 65 |  |  | K | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
828 | 01PGA42AA001 | RDST-00-PG_-MDD-EAI-12200 | I | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA42BR002 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
829 | 01PGA42AA002 | RDST-00-PG_-MDD-EAI-12200 | I | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA42BR003 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
830 | 01PGA53AA001 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA53BR001 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
831 | 01PGA53AA002 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA53BR002 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
832 | 01PGA53AA003 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA53BR003 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
833 | 01PGA53AA004 | RDST-00-PG_-MDD-EAI-12200 | I | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA53BR004 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24400 |  | CS-LU-IC3 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
834 | 01PGA41AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA41BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
835 | 01PGA41AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 80 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA41BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
836 | 01PGA51AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA51BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
837 | 01PGA51AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA51BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
838 | 01PGA71AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA71BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
839 | 01PGA71AA003 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA71BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
840 | 01PGA71AA004 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA71BR004 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
841 | 01PGA71AA005 | RDST-00-PG_-MDD-EAI-12200 | E | 65 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA71BR005 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
842 | 01PGA56AA007 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA56BR012 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
843 | 01PGA56AA008 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA56BR013 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
844 | 01PGA57AA007 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA57BR012 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
845 | 01PGA57AA008 | RDST-00-PG_-MDD-EAI-12200 | E | 100 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA57BR013 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
846 | 01PGA58AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 150 mm | Butterfly valve | A-536 Gr 60-40-18 | AA6MW | CL150 | WL | STD | 01PGA58BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24400 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
847 | 01PGA10AA501 | RDST-00-PG_-MDD-EAI-12200 | I | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA10BR501 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
848 | 01PGA10AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA10BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
849 | 01PGA20AA501 | RDST-00-PG_-MDD-EAI-12200 | I | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA20BR501 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
850 | 01PGA20AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA20BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
851 | 01PGA30AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA30BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
852 | 01PGA30AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA30BR501 | DWater/P.Glycol | 0.49 | 60 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
853 | 01PGA30AA003 | RDST-00-PG_-MDD-EAI-12200 | E | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA30BR503 | DWater/P.Glycol | 0.49 | 60 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
854 | 01PGA30AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA30BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
855 | 01PGA30AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA30BR703 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
856 | 01PGA40AA501 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA40BR501 | Air-DWater/PG | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
857 | 01PGA40AA704 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA40BR704 | DWater/P.Glycol | 8 | 65 |  |  |  | 30 mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
858 | 01PGA40AA705 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA40BR705 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
859 | 01PGA44AA501 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA44BR501 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
860 | 01PGA44AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA44BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
861 | 01PGA46AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA46BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
862 | 01PGB40AA502 | RDST-00-PG_-MDD-EAI-12200 | E | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB40BR502 | Air-DWater/PG | 8 | 68 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
863 | 01PGB44AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB44BR703 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
864 | 01PGB46AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB46BR703 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
865 | 01PGB50AA501 | RDST-00-PG_-MDD-EAI-12200 | I | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB50BR501 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
866 | 01PGB50AA502 | RDST-00-PG_-MDD-EAI-12200 | I | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB50BR502 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
867 | 01PGB51AA501 | RDST-00-PG_-MDD-EAI-12200 | I | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR501 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
868 | 01PGB51AA502 | RDST-00-PG_-MDD-EAI-12200 | I | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR502 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
869 | 01PGB50AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB50BR701 | Air-DWater/PG | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
870 | 01PGB50AA702 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB50BR702 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
871 | 01PGB50AA703 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB50BR703 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
872 | 01PGB51AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR701 | Air-DWater/PG | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
873 | 01PGB51AA702 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR702 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
874 | 01PGB51AA703 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB51AA703 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
875 | 01PGB50AA503 | RDST-00-PG_-MDD-EAI-12200 | I | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB50BR503 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
876 | 01PGB51AA503 | RDST-00-PG_-MDD-EAI-12200 | I | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR503 | Air-DWater/PG | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
877 | 01PGE01AA501 | RDST-00-PG_-MDD-EAI-12200 | E | 50 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGE01BR001 | DWater/P.Glycol | 8 | 65 |  |  | K | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
878 | 01PGE01AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 40 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGE01BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
879 | 01PGE01AA702 | RDST-00-PG_-MDD-EAI-12200 | E | 40 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGE01BR702 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
880 | 01PGE01AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 50 mm | Ball valve | A-105 | AA1BF | CL150 | FL | STD | 01PGE01BR703 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
881 | 01PGE01AA704 | RDST-00-PG_-MDD-EAI-12200 | E | 50 mm | Ball valve | A-105 | AA1BF | CL150 | FL | STD | 01PGE01BR704 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
882 | 01PGE01AA705 | RDST-00-PG_-MDD-EAI-12200 | E | 50 mm | Ball valve | A-105 | AA1BF | CL150 | FL | STD | 01PGE01BR705 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032 |  |  |  | 配供螺栓、螺母、垫片、密封垫
883 | 01PGA42AA501 | RDST-00-PG_-MDD-EAI-12200 | I | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA42BR501 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
884 | 01PGA42AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA42BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
885 | 01PGA43AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA43BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
886 | 01PGA45AA501 | RDST-00-PG_-MDD-EAI-12200 | I | 25 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | XS | 01PGA45BR501 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
887 | 01PGA45AA502 | RDST-00-PG_-MDD-EAI-12200 | I | 20 mm | Ball Valve, closed | A-105 | AD1BR | CL600 | TH | STD | 01PGA45BR502 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
888 | 01PGA55AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA55BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
889 | 01PGA55AA704 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA55BR704 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
890 | 01PGB42AA704 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB42BR704 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
891 | 01PGB43AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB43BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
892 | 01PGB55AA701 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB55BR701 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
893 | 01PGB55AA702 | RDST-00-PG_-MDD-EAI-12200 | I | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB55BR702 | DWater/P.Glycol | 8 | 65 | [5 empty] | 478-00-SV-M-24420 |  | CS-LU-IC3 | 6032
894 | 01PGA41AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA41BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
895 | 01PGA41AA702 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA41BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
896 | 01PGA51AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA51BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
897 | 01PGA51AA702 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA51BR702 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
898 | 01PGA71AA006 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA71BR006 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
899 | 01PGA71AA007 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA71BR007 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
900 | 01PGA71AA008 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA71BR008 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
901 | 01PGA71AA009 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA71BR009 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
902 | 01PGA71AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA71BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
903 | 01PGA72AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA72BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
904 | 01PGA72AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA72BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
905 | 01PGA72AA003 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA72BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
906 | 01PGA72AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA72BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
907 | 01PGB41AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB41BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
908 | 01PGB41AA702 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB41BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
909 | 01PGB51AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
910 | 01PGB51AA702 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB51BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
911 | 01PGB71AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB71BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
912 | 01PGB72AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB72BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
913 | 01PGA56AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA56BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
914 | 01PGA57AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA57BR003 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
915 | 01PGB56AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB56BR003 | Air-DWater/PG | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
916 | 01PGB57AA703 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB57BR003 | Air-DWater/PG | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
917 | 01PGA48AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA48BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
918 | 01PGA48AA001 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA48BR001 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
919 | 01PGA48AA002 | RDST-00-PG_-MDD-EAI-12200 | E | 25 mm | Ball valve | A-105 | AD1BS | CL600 | SW | STD | 01PGA48BR002 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
920 | 01PGB48AA702 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB48BR702 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
921 | 01PGA58AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGA58BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032
922 | 01PGB58AA701 | RDST-00-PG_-MDD-EAI-12200 | E | 15 mm | Ball valve | A-105 | AD1BR | CL600 | TH | XS | 01PGB58BR701 | DWater/P.Glycol | 8 | 65 |  |  |  | 30mm |  | 478-00-SV-M-24420 |  | CS-LU-WC4 | 6032