Name and range of application

  - This requirement specification establishes requirements and determines conditions of purchase of a centrifugal pump unit (single stage, spiral, with a horizontal casing split and the impeller of a bilateral inlet, complete with spare parts and technical documentation.

The unit pumps thermal clamping water in a heating system.

- Technical requirements

| Technical data | Parameter |
| --- | --- |
| Flow (not less), m3/h | 1250 |
| Head (not less), m | 70 |
| NPSH, m | 3.8 |
| Allowable differential pressure at pump inlet, (no more) MPa | 0.35 |

| Physical properties | Parameter |
| --- | --- |
| Temperature, 0 C | 40-85 °C |
| Density, kg/m3 | 968 - 990 |
| Solids content, no more than, mg/l | 5 |
| Size of solids, no more than, mm. | 0.2 |

Water temperature fed to cool of bearing units: 14-21 °C.

Ambient temperature: -10/+40 °C.

Motor:

- 6000V. 50Hz

- Class insulation: F at least

- grease replenishment and removal system without stopping and disassembling the motor is required

- bearings on the drive side and on the opposite side - ball bearings

- the location of the input device is on top

- possibility of rearranging the input device - 2 x 180⁰

- start method - directly from the power line

- spare parts: spare bearing set

- metallic cooling fan

- Scope of supply

  - Scope of delivery must include:

- pump unit assembled (the pump with the coupling and the electric motor on a frame) - 1 set

- connecting counterflanges on suction and discharge lines with hardwarefixture - 1 set.

- spare parts: protective shaft sleeve - 2 pieces; sealings (cups, rubber rings) needed for technical maintenance and repair - 2 sets; elastic sleeves of coupling - 2 sets; a gasket of casing split and cover - 2 pieces.

- Design requirements

  - The unit is centrifugal, horizontal, spiral, with a horizontal casing split, singlestage with the impeller of a bilateral inlet.

  - Direction of rotor rotation - clockwise if to look from the side of the electric motor.

  - Rotor is supported by outer rolling bearings with oil-bath lubrication.

  - Bearing housings of the pump must have a water cooling jacket of wet sump and nozzles for feed and withdrawal of a cooling water.

  - Shaft seals with stuffing box.

  - Coupling between pump and electric motor must be steel pin bush coupling type.

  - Parts of flow channel of the pump must be cast iron, a shaft and the impeller - from chrome steel. Production of impeller bronze is allowed.

  - The pump must be mounted on a single frame with the electric motor.

- Requirements to an electrical equipment.

  - Requirements for electrical equipment are listed below.

- Requirements of reliability

  - Reliability of the unit at operating conditions must be characterized by the following:

- the average time between failures must be 10000 hours at least.

- life cycle - not less than 20 years.

  - Compliance of the unit to requirements for reliability is evaluated according to GOST 27.002-89, GOST 27.003-89, GOST 27.301-95, GOST 27.410-87.

- Safety requirements and environmental protections

  - The middle tier of sound pressure and middle tier of a sound, at nominal operating conditions must not exceed 105 dB.

- Requirements of compatibility

  - The unit must pump thermal clamping water with the properties stated above.

- Requirements to technical documentation

  - Technical documentation must include:

- the maintenance manual on the unit;

- the passport of the unit (or the form included in the maintenance manual);

- passport of the electric motor;

- the passport of each block, device, measuring instrument (in case of presence);

- measurement units, values (material grades) of the functional characteristics should be brought to the specified in the requirement specification.

  - Maintenance manual must include additionally:

- required types of repairs;

- quantity and sequence of accomplishment of repairs of different types;

- specified life before repair of each type;

- ineffective time (in hours) of the unit during each repair type;

- typical failures, reasons, elimination methods;

- allowable value of a residual unbalance of a rotor;

- vibration frequencies by which it is possible to identify failures of the unit by means of the frequency analysis;

- assembly drawing. On assembly drawings of the pump and its separate blocks the dimensions, tolerances on dimensions, clearances and tensions, necessary and sufficient for high-quality repair of the pump and all its components during operation, must be indicated. Assembly drawings of bearing units;

- at consumption rates analogs of lubricants must be specified;

- instructions for installation, start-up, regulation and run-in;

- list of parts and assembly units;

- list of spare parts, tools, acclimations.

  - In case of impossibility to include any of items mentioned above in the maintenance manual, please provide the separate document in which the required information is stated.

  - The seller should provide:

- the letter of indemnity confirming providing copies of acts of incoming control of materials and components, submission of copies of test reports at the time of delivery of an equipment.

- Order of monitoring and acceptance

  - Incoming control of materials and components must be made on manufacturing plant in accordance with the established procedure with providing copies of the acts.

  - Acceptance tests are made at the buyer plant.

  - The unit must undergo standard testing at manufacturing plant with providing copies of the acts.