# Part 2 – Supply Requirements

Section VII - Schedule of Requirements

Contents

# 1. List of Goods and Delivery Schedule	Error! Bookmark not defined.

# 2. List of Related Services and Completion Schedule	151

# 3. Technical Specifications	152

# 4. Drawings	187

# 5. Inspections and Tests	188

## Notes for Preparing the Schedule of Requirements

The Schedule of Requirements shall be included in the bidding document by the Purchaser, and shall cover, at a minimum, a description of the goods and services to be supplied and the delivery schedule.

The objective of the Schedule of Requirements is to provide sufficient information to enable Bidders to prepare their Bids efficiently and accurately, in particular, the Price Schedule, for which a form is provided in Section IV. In addition, the Schedule of Requirements, together with the Price Schedule, should serve as a basis in the event of quantity variation at the time of award of contract pursuant to ITB 42.1.

The date or period for delivery should be carefully specified, taking into account (a) the implications of delivery terms stipulated in the Instructions to Bidders pursuant to the Incoterms rules (i.e., EXW, or CIP, FOB, FCA terms—that “delivery” takes place when goods are delivered to the carriers), and (b) the date prescribed herein from which the Purchaser’s delivery obligations start (i.e., notice of award, contract signature, opening or confirmation of the letter of credit).

LOT II

Supply of  Spare Parts and Commissioning for Rehabilitation of substations in the Inter-Connected System

1. List of Goods and Delivery Schedule

| Line Item No. | Description of Goods | Unit | Quantity | Final Destination (Project Site) as specified in BDS |  | Delivery (as per Incoterms) Date |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Earliest Delivery Date | Latest Delivery Date | Bidder’s offered Delivery date [to be provided by the Bidder] |
|  |  |  |  | As per ITB 14.9 (b)(i) |  | 5 months after contract signing | 6 months after contract signing |  |
|  | Three phase 132 KV SF6 Circuit breaker | ea | 3 |  |  |  |  |  |
|  | Spare closing coils for 132 KV breaker in item 2 | ea | 5 |  |  |  |  |  |
|  | Spare opening with tripping coils for 132 KV breaker in item 2 | Ea | 5 |  |  |  |  |  |
|  | Charging electric motor for the 132 kV circuit breakers in item 2 | Ea | 3 |  |  |  |  |  |
|  | Three phase single pole 132 KV CTs | Ea | 9 |  |  |  |  |  |
|  | Three phase single pole 132 KV Inductive VTs | Ea | 3 |  |  |  |  |  |
|  | Three phase 66 KV SF6 Circuit breaker | Ea | 15 |  |  |  |  |  |
|  | Spare closing coils for 66 KV breaker in item 7 | Ea | 5 |  |  |  |  |  |
|  | Spare opening with tripping coils for 66 KV breaker in item 7 | Ea | 5 |  |  |  |  |  |
|  | Charging electric motor for the 66 kV circuit breakers in item 7 | Ea | 5 |  |  |  |  |  |
|  | Three phase single pole 66 KV CTs | Ea | 15 |  |  |  |  |  |
|  | Three phase single pole 66 KV Inductive VTs | Ea | 9 |  |  |  |  |  |
|  | MV Equipments |  |  |  |  |  |  |  |
|  | 15KV Switchgear Panel consisting of - One transformer incoming cubicle, with electrically and manually driven withdrawable vacuum circuit breaker of 1250A. (Cubicle must include transformer and bus bar protection relays, other protection relays, CTs, PTs, Energy meters, Amper meters … etc) - And six feeder line cubicles with electrically and manually driven withdrawable vacuum circuit breaker of 630A (each cubicle must include protection relays, CTs, PTs, Energy meters, Amper meters … etc) (Kindly refer to the specification section for detailed specifications of each cubicle) | set | 4 sets |  |  |  |  |  |
|  | Stand-alone three phase 15 KV feeder cubicle with electrically and manually driven withdrawable vacuum circuit breaker of 630A. | Ea | 6 |  |  |  |  |  |
|  | Stand-alone three phase 15 KV feeder cubicle with electrically and manually driven withdrawable vacuum circuit breaker of 1250A. | Ea | 3 |  |  |  |  |  |
|  | Stand-alone three phase 15 KV transformer incoming cubicle with electrically and manually driven withdrawable vacuum circuit breaker of 1250A. | Ea | 3 |  |  |  |  |  |
|  | Stand-alone 15 KV Bus Coupler, with electrically and manually driven withdrawable vacuum circuit breaker of 2500A. | Ea | 2 |  |  |  |  |  |
|  | three phase 15 KV Spare vacuum CB, 1250 A | Ea | 3 |  |  |  |  |  |
|  | three phase 15 KV Spare vacuum CB, 630 A | Ea | 5 |  |  |  |  |  |
|  | Spare 15 KV Voltage Transformer (Indoor) | Ea | 10 |  |  |  |  |  |
|  | Spare 15 KV Current Transformer (Indoor) | Ea | 20 |  |  |  |  |  |
|  | Protection Systems |  |  |  |  |  |  |  |
|  | Multifunction data recording and communication module | Ea | 10 |  |  |  |  |  |
|  | Digital multifunction transformer differential protection relay | Ea | 20 |  |  |  |  |  |
|  | Microprocessor overcurrent and earth fault protection relay + auto reclose | Ea | 20 |  |  |  |  |  |
|  | Microprocessor overcurrent and differential earth fault protection relay + auto reclose | Ea | 30 |  |  |  |  |  |
|  | Modular low impedance bus bar protection | Ea | 5 |  |  |  |  |  |
|  | Relays interfacing program | Ea | 5 |  |  |  |  |  |
|  | Zero sequence overcurrent relay | Ea | 5 |  |  |  |  |  |
|  | High impedance deferential Relays | Ea | 5 |  |  |  |  |  |
|  | Lock-out Relays | Ea | 10 |  |  |  |  |  |
|  | Trip circuit supervision relay | Ea | 40 |  |  |  |  |  |
|  | The DLP digital relaying system for single and three pole tripping application | Ea | 10 |  |  |  |  |  |
|  | DLP1112KDH | Ea | 12 |  |  |  |  |  |
|  | Multifunction microprocessor synchrocheck relay | Ea | 10 |  |  |  |  |  |
|  | Matrix Interfacing module | Ea | 5 |  |  |  |  |  |
|  | Protection panel 66 KV &132 KV (Optional) | Ea | 12 |  |  |  |  |  |
|  | Power transformers |  |  |  |  |  |  |  |
|  | 6 MVA, 66/15 KV Power transformer | Ea | 6 |  |  |  |  |  |
|  | Auxiliary back-up power supply system |  |  |  |  |  |  |  |
| 1 | Battery Bank with charger | Ea | 15 |  |  |  |  |  |
|  | Communication equipments |  |  |  |  |  |  |  |
| - 1 | Walkie-Talkie radio repeaters for communication between the power plants and substations, as well as for line men | Ea | 2 |  |  |  |  |  |
|  | long range two-way radio walkie talkie | Ea | 20 |  |  |  |  |  |
|  | long range car mounted base station walkie talkie radio | Ea | 30 |  |  |  |  |  |
|  | MV Cables and Termination tool kit |  |  |  |  |  |  |  |
| 1 | 240 mm2 15 KV CABLE | m | 1000 m |  |  |  |  |  |
| 2 | 120 mm2 15 KV CABLE | m | 1000 m |  |  |  |  |  |
| 3 | Cable Termination kit | ea | 1000 |  |  |  |  |  |
| 4 | Tabular Cable lug | m | 500 for 240 mm2 cable 500 for 120 mm2 cable |  |  |  |  |  |
| 5 | HV Cable stripping tool | ea | 4 |  |  |  |  |  |
| 6 | Cable lug compressing tool | ae | 4 |  |  |  |  |  |
|  | PPE |  |  |  |  |  |  |  |
| 1 | Safety Helmet | ea | 500 |  |  |  |  |  |
| 2 | Safety goggles | ea | 500 |  |  |  |  |  |
| 3 | Face shield for welders with specialized tints | ea | 30 |  |  |  |  |  |
| 4 | Ear plug (typically 85 Dba) | ea | 2000 |  |  |  |  |  |
| 5 | Insulating gloves (1KV) | ea | 500 |  |  |  |  |  |
| 6 | General gloves (cut resistant for handling rough or sharp materials) | ea | 2000 |  |  |  |  |  |
| 7 | Chemical resistant gloves for handling lubricants or corrosive substances | ea | 500 |  |  |  |  |  |
| 8 | Thermal gloves: for handling pipes, steam lines, or boiler | ea | 500 |  |  |  |  |  |
| 9 | Flame resistant clothing | ea | 50 |  |  |  |  |  |
| 10 | High visibility vest | ea | 2000 |  |  |  |  |  |
| 11 | Fall protection belt | ea | 30 |  |  |  |  |  |
| 12 | First aid kit | ea | 30 |  |  |  |  |  |

| 2. List of Related Services and Completion Schedule [This table shall be filled in by the Purchaser. The Required Completion Dates should be realistic, and consistent with the required Goods Delivery Dates (as per Incoterms)] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Service | Description of Service | Quantity1 | Physical Unit | Place where Services shall be performed | Final Completion Date(s) of Services |
| [insert Service No] | [insert description of Related Services] | [insert quantity of items to be supplied] | [insert physical unit for the items] | [insert name of the Place] | [insert required Completion Date(s)] |
| 1 | Installation and Commissioning supervision of protection systems |  |  | Final destination as specified in BDS ITB 14.9 | 6 months from delivery date |
| 2 |  |  |  | Final destination as specified in BDS ITB 14.9 |  |
| 1. If applicable |  |  |  |  |  |

3. Technical Specifications

Spare parts for Rehabilitation and Commissioning of Substations in the Inter-Connected System

- HV Equipments

Note: All 132 kV and 66 kV circuit breakers (CBs), current transformers (CTs), and Voltage transformers (VTs) will be supplied without supporting structures. These components are intended to be mounted on the existing support structures, the detailed dimensions of which are provided in the mechanical specifications of each item in this bidding document. Bidders must therefore ensure their manufactured components precisely fit these existing structures as per the attached drawings.

- 132 KV Circuit breaker

| No. | Item | Unit | Employer requirements | Vendor data |
| --- | --- | --- | --- | --- |
| 132 KV Circuit breaker |  |  |  |  |
|  | Manufacturer |  | ABB or equivalent |  |
|  | Origin of manufacturer |  |  |  |
|  | Quantity (Three phase with one common base) | set | 3 |  |
|  | Type of arc quenching medium |  | SF6 |  |
|  | Specific Creepage Distance (SCD) | mm/KV | 31 |  |
|  | Arrangement |  | outdoor |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated current | A | 630 |  |
|  | Rated voltage | KV | 170 |  |
|  | Impulse withstand Voltage | KV | 750 |  |
|  | Nominal system voltage Un RMS phase to phase (Uo/U) | KV | 76.3/132 |  |
|  | Max. continuous system voltage | kV | 145 |  |
|  | Rated power frequency withstands voltage | KV | 325 |  |
|  | Phase discrepancy | KA | 8 |  |
|  | Breaking capability | KA | 31.5 |  |
|  | Standard insulation level | KV | 275-650 |  |
|  | Circuit breaker drive | - | motor |  |
|  | Circuit breaker rated operating sequence | - | O-0.3s-CO-1min-CO |  |
|  | SF6 mass | Kg | - |  |
|  | SF6 leakage/annum |  | <= 1% |  |
|  | Circuit breaker mass | Kg | <= 1900 |  |
|  | Coils: |  |  |  |
|  | Supply voltage for drive(coils) | V dc | 110(+10% -30%) |  |
|  | Electric motor drive type |  | spring-charged motor-driven with provision for manual operation |  |
|  | Power | W | - |  |
|  | Resistance (at 20℃) | Ω | <=30±10% |  |
|  | Quantity |  | Closing= 1 Opening/tripping= 2 |  |
|  | Motor |  |  |  |
|  | U nominal | Vdc | 110 |  |
|  | Power | W | - |  |
|  | Anticondensation supply |  |  |  |
|  | V. nominal | Vac | 230(+10% -15%) |  |
|  | Power | W |  |  |
|  | Standards applied | IEC | IEC 61869 |  |
|  | Quality control | ISO | 9001 |  |
|  | Height of CB | mm |  |  |
|  | Clearance between poles | mm |  |  |

## Mechanical Specifications (Bidder to adhere to the specifications to ensure structural compatibility and smooth replacement)

| Parameter | Specification |
| --- | --- |
| Overall Height | Approx. 2500-2700 mm |
| Base flange size | 295 mm x 295 mm |
| Base frame size | 1190 mm x 680 mm x 350 mm (cabinet frame) |
| Pole Centers | 200 mm |
| Foundation Bolt Pattern | 4 main mounting holes per leg |
| Bolt Hole Diameter | Ø20 mm (for M18 bolts) |
| Material | Steel frame, SF6 insulated poles |
| Weight | 1600 kg |
| Operating Temperature | -25°C to +45°C |
| Standard | IEC 62271-100 |

- 132 KV CURRENT TRANSFORMER

| No. | Items | Unit | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| 132 KV CURRENT TRANSFORMER |  |  |  |  |
|  | Origin of manufacture | - | ABB or equivalent |  |
|  | Type | - | Outdoor, Oil immersed |  |
|  | Quantity (single pole with all accessories) | each | 9 |  |
|  | Specific Creepage Distance | mm/kV | 31 |  |
|  | Arrangement |  | outdoor |  |
|  | Rated frequency | Hz | 50 |  |
|  | Highest system voltage | KV | 145 |  |
|  | Rated primary voltage | KV | 132√3 |  |
|  | Temperature range | ℃ | -40 - +40 |  |
|  | Rated current | A | 300-600 |  |
|  | Secondary rated current | A | 1 |  |
|  | Short time thermal current (Ith) | KA | 31.5 for 3S |  |
|  | Max. elevation | M | 2500 |  |
|  | Total mass | Kg | <= 685 |  |
|  | Insulation level | kV | 325-750 |  |
|  | Short circuit withstand capability | kA | 31.5 |  |
|  | Ratio | A | 300-600/1/1/1/1 |  |
|  | Accuracy class: |  | 0.2S/0.5 for metering, 5P/10P for protection. |  |
|  | Total height of the CT | mm | 2765 |  |
|  | Protection class | - | 5P20 |  |
|  | Burden | VA | 50 |  |
|  | Standards applied | IEC | IEC 61869 |  |
|  | Quality control | ISO | ISO 9001 |  |

## Mechanical Specifications (Bidder to adhere to the specifications to ensure structural compatibility and smooth replacement)

| Parameter | Specification |
| --- | --- |
| Overall Height | Approx. 2765 mm |
| Porcelain height | 1330 mm |
| Base to top of secondary box | 795 mm |
| Base Flange Size | 410 mm x 410 mm |
| Bolt Hole Circle Diameter (PCD) | 345 mm |
| Number of Bolt Holes | 4 (at 90° intervals) |
| Bolt Hole Diameter | Ø18 mm (for M16 bolts) |
| Distance between bolt holes | 300 mm |
| Mounting Type | Flange mounted, outdoor design |
| Material | Porcelain insulator with hot-dip galvanized steel base |
| Weight | 685 kg |
| Oil mass | 70 kg |
| Creepage Distance | 3555 mm |
| Operating Temperature | -40°C to +45°C |
| Standard | IEC 44-1 |

- 66 KV Circuit breaker

| No | Item | Unit | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| 66 KV Circuit breaker |  |  |  |  |
|  | Manufacturer | - | ABB or equivalent |  |
|  | Origin of manufacturer |  |  |  |
|  | Quantity (Three phase with one common base) | set | 15 |  |
|  | Type of quenching medium | - | SF6 |  |
|  | Specific Creepage Distance (SCD) | mm/KV | 31 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Rated current | A | 630 |  |
|  | Nominal system voltage Uo/U | kV | 38.1/66 |  |
|  | Highest system operating voltage U max. | kV | 72.5 |  |
|  | Rated power frequency withstands voltage rms | KV | 140 |  |
|  | Impulse withstand voltage | KV | 325 |  |
|  | Breaking capability | KA | 20 |  |
|  | Phases discrepancy | KA | 8 |  |
|  | Breaking factor |  | 1.5 |  |
|  | Between line terminal and ground | kV | 162.5 |  |
|  | Between terminals with CB open | kV | 186 |  |
|  | Insulation level |  |  |  |
|  | SF6 pressure at 20℃ | MPA | 0.7 |  |
|  | SF6 mass | Kg | - |  |
|  | SF6 leakage/annum | % | <= 1 |  |
|  | Circuit breaker mass | Kg | - |  |
|  | Drive supply |  |  |  |
|  | Motor drive type |  | spring-charged motor-driven with provision for manual operation |  |
|  | Coils: |  |  |  |
|  | Voltage U | Vdc | 110 (+10% -30%) |  |
|  | Power | W | - |  |
|  | Resistance (at 20℃) | Ω | 30±10% |  |
|  | Quantity |  | Closing= 1 Opening/tripping= 2 |  |
|  | Motor |  |  |  |
|  | U nominal | Vdc | 110 |  |
|  | Power | W | - |  |
|  | Anticondensation supply |  |  |  |
|  | U. nominal | Vac | 220(+10% -15%) |  |
|  | Power | W | - |  |
|  | Standards applied | IEC | IEC 62271 |  |
|  | Quality control | ISO | ISO 9001 |  |
|  | Height | mm |  |  |
|  | Clearance between poles | mm |  |  |

## Mechanical Specifications (Bidder to adhere to the specifications to ensure structural compatibility and smooth replacement)

| Parameter | Specification |
| --- | --- |
| Overall Height | Approx. 2300 mm |
| Base Frame Size | 295 mm x 295 mm |
| Base Frame Size | 1190 mm x 680 mm x 350 mm (cabinet frame) |
| Pole Centers | 200 mm |
| Foundation Bolt Pattern | 4 main mounting holes per leg |
| Bolt Hole Diameter | Ø20 mm (for M18 bolts) |
| Material | Steel frame, SF6 insulated poles |
| Weight | 1600 kg |
| Operating Temperature | -25°C to +45°C |
| Standard | IEC 62271-100 |

- 66 KV CURRENT TRANSFORMER

| No. | Items | Units | Design requirements | Vender data |
| --- | --- | --- | --- | --- |
| 66 KV CURRENT TRANSFORMER |  |  |  |  |
|  | Origin of manufacture | - | ABB or equivalent |  |
|  | Type | - | Outdoor, Oil immersed |  |
|  | Quantity (single pole with all accessories) | Each | 14 |  |
|  | Specific Creepage Distance (SCD) | mm/kV | 31 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Nominal system voltage Un | kV | 66 |  |
|  | Highest system operating voltage U max. | kV | 72.5 |  |
|  | Rated power frequency withstands voltage rms | kV | 162.5 |  |
|  | Insulation level | KV | 230-550 |  |
|  | Short circuit withstand capability | A | 31.5 for 3s |  |
|  | Max. cont. thermal current | A | 200 – 400 |  |
|  | Secondary rated current | A | 1 A= (Quantity 7) 5 A= (Quantity 7) |  |
|  | Number of windings | No. | 4 |  |
|  | Max. elevation | M | 2500 |  |
|  | Thermal current Ith | KA/1s | 12-12 |  |
|  | Idyn | KA | 30-30 |  |
|  | Accuracy |  | Protection Class= 5P20 Metering class= 0.5/0.2S |  |
|  | Burden | VA | 50 |  |
|  | Standards applied | IEC | IEC 61869 |  |
|  | Quality control | ISO | ISO 9001 |  |
|  | Height | mm | 2365 |  |

## Mechanical Specifications (Bidder to adhere to the specifications to ensure structural compatibility and smooth replacement)

| Parameter | Specification |
| --- | --- |
| Overall Height | Approx. 1940 mm |
| Porcelain Height | 980 mm |
| Base to top of secondary box | 795 mm |
| Base Flange Size | 410 mm x 410 mm |
| Bolt Hole Circle Diameter (PCD) | 345 mm |
| Number of Bolt Holes | 4 (at 90° intervals) |
| Bolt Hole Diameter | Ø18 mm (for M16 bolts) |
| Distance between bolt holes | 300 mm |
| Mounting Type | Flange mounted, outdoor design |
| Material | Porcelain insulator with hot-dip galvanized steel base |
| Weight | 615 kg |
| Oil mass | 65 kg |
| Creepage Distance | 3160 mm |
| Operating Temperature | -40°C to +45°C |
| Standard | IEC 44-1 |

- 132 kV single pole inductive voltage transformer

| No. | Items | Units | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| 132 KV single pole inductive voltage TRANSFORMER |  |  |  |  |
|  | Origin of manufacture | - | ABB or equivalent |  |
|  | Type of voltage transformer | - | Inductive |  |
|  | Quantity (Single pole) | each | 9 |  |
|  | Specific Creepage Distance (SCD) | mm/kV | 31 |  |
|  | Arrangement |  | outdoor |  |
|  | No. of phases |  | Single |  |
|  | Rated frequency | Hz | 50 |  |
|  | Nominal system voltage | KV | 132 |  |
|  | Max. system voltage | KV | 145 |  |
|  | Max. simultaneously burden | VA | 250 |  |
|  | Altitude | M | 2500 |  |
|  | Ambient temperature | ℃ | -5 - +55 |  |
|  | Pollution level |  | high |  |
|  | Power frequency withstand voltage | kV | 325 |  |
|  | Impulse withstand Voltage | KV | 750 |  |
|  | Burden | VA | 50 |  |
|  | Insulation level | KV | 275-650 |  |
|  | Insulation class |  | Class A outdoor type |  |
|  | Number of cores | 3 | 3 |  |
|  | Accuracy class |  | Protection Class= 5P20 Metering class= 0.5/0.2S |  |
|  | Earth terminal |  | Provided |  |
|  | Standards applied | IEC |  |  |
|  | Quality control | ISO |  |  |
|  | Height |  | 2670 |  |

## Mechanical Specifications (Bidder to adhere to the specifications to ensure structural compatibility and smooth replacement)

| Parameter | Specification |
| --- | --- |
| Overall Height | Approx. 2670 mm |
| Porcelain height | 1440 mm |
| Base Flange Size | 600 mm x 600 mm |
| Bolt Hole Circle Diameter (PCD) | 540 mm |
| Number of Bolt Holes | 4 (at 90° intervals) |
| Bolt Hole Diameter | Ø28 mm (for M24 bolts) |
| Distance between bolt holes | 390 mm |
| Mounting Type | Flange mounted, outdoor design |
| Material | Porcelain insulator with galvanized steel base |
| Weight | 620 kg |
| Oil mass | 90 kg |
| Creepage Distance | 4670 mm |
| Operating Temperature | -40°C to +45°C |
| Standard | IEC 186 |

- 66 kV single pole inductive voltage transformer

| No. | Items | Units | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| 66 KV single pole inductive voltage TRANSFORMER |  |  |  |  |
|  | Origin of manufacture | - | Vendor Data |  |
|  | Type of voltage transformer | - | Inductive |  |
|  | Quantity (Single pole) | each | 15 |  |
|  | Specific Creepage Distance (SCD) | mm/kV | 31 |  |
|  | Arrangement |  | outdoor |  |
|  | No. of phases |  | Single |  |
|  | Rated frequency | Hz | 50 |  |
|  | Nominal system voltage | KV | 66/3 |  |
|  | Max. system voltage | KV | 72.5 |  |
|  | Max. simultaneously burden | VA | 250 |  |
|  | Altitude | M | 2500 |  |
|  | Ambient temperature | ℃ | -5 - +55 |  |
|  | Pollution level |  | high |  |
|  | Power frequency withstand voltage | kV | 140 |  |
|  | Impulse withstand voltage | KV | 325 |  |
|  | Burden | VA | 50 |  |
|  | Insulation level | KV KV | 140-350 275-650 |  |
|  | Insulation class |  | Class A outdoor type |  |
|  | Number of cores |  | 3 |  |
|  | Accuracy class |  |  |  |
|  | Earth terminal |  | Provided |  |
|  | Standards applied | IEC |  |  |
|  | Quality control | ISO |  |  |
|  | Height | mm | 1515 |  |

## Mechanical Specifications (Bidder to adhere to the specifications to ensure structural compatibility and smooth replacement)

| Parameter | Specification |
| --- | --- |
| Overall Height | Approx. 1575 mm |
| Base Flange Size | 320 mm x 320 mm |
| Bolt Hole Circle Diameter (PCD) | 280 mm |
| Number of Bolt Holes | 4 (at 90° intervals) |
| Bolt Hole Diameter | Ø18 mm (for M16 bolts) |
| Mounting Type | Flange mounted, outdoor design |
| Material | Porcelain insulator with galvanized steel base |
| Weight | 190 kg |
| Oil mass | 25 kg |
| Creepage Distance | 2060 mm |
| Operating Temperature | -40°C to +45°C |
| Standard | IEC 186 |

- Closing coil for the 132 & 66 kV circuit breaker (Spare for the above breakers)

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| Closing coil for the 132/66 kV circuit breaker |  |  |  |  |
|  | Coil: | - |  |  |
|  | Quantity | set | 15 for 66 KV and 15 for 132 KV |  |
|  | Supply voltage for drive(coils) nominal | V dc | 110(+10% -30%) |  |
|  | Power | w | - |  |
|  | Resistance (at 20℃) | Ω | <= 30±10% |  |

- Opening with Tripping coil for the 132 & 66 kV circuit breaker (Spare for the above breakers)

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| Opening with Tripping coil for the 132/66 kV circuit breaker |  |  |  |  |
|  | Coil: | - |  |  |
|  | Quantity | set | 15 for 66 KV and 15 for 132 KV |  |
|  | Supply voltage for drive(coils) nominal | V dc | 110(+10% -30%) |  |
|  | Power | W | - |  |
|  | Resistance (at 20℃) | Ω | <= 30±10% |  |

NB: Opening, tripping and closing coils for 66 KV and 132 KV shall be of identical specifications as in the breakers.

- Charging electric motor for the 132/66 kV circuit breakers (Spare to the above HV Circuit Breakers)

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| Charging electric motor for the 132 & 66 kV circuit breaker |  |  |  |  |
|  | Motor Type |  | Permanent Magnet DC Motor |  |
|  | Quantity |  | 132 KV CB= 10 66 KV CB= 10 |  |
|  | Model / Type |  | - |  |
|  | Serial Number |  | - |  |
|  | Rated Power | W | - |  |
|  | Rated Voltage | Vdc |  |  |
|  | Rated Speed | rpm | 3000 |  |
|  | Rated Current | A |  |  |
|  | Duty Type |  | S1 (Continuous Duty) |  |
|  | Insulation Class |  | Class A |  |
|  | Cooling |  | Self-ventilated (based on casing) |  |
|  | Applicable Standards |  | CEI 2-4 (1957); CEI 2-3 (1988) |  |

- MV Equipments

- 15 KV Feeder Cubicle

NB: Please adhere to the List of Goods and Delivery Schedule regarding MV cubicles quantities.

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| 15 KV Feeder Cubicle 1520/ 2500 A |  |  |  |  |
|  | Manufacturer | - |  |  |
|  | Origin of manufacture |  |  |  |
|  | Type | - | Metal-clad, metal-enclosed, indoor floor-mounting, free-standing cubicle |  |
|  | Type of circuit breaker (vacuum) (Refer item No. 11 for breaker specifications) | - | Vacuum |  |
|  | Protection class indoor panels | IP | 41 |  |
|  | Protection relays (earth fault, overcurrent… etc) | - | Provided |  |
|  | Energy meter | - | Provided |  |
|  | Rated system voltage | kV | 15 |  |
|  | Max. system rated voltage | kV | 24 |  |
|  | Rated power frequency withstand voltage, rms value, kV during 1 mn | kV | 44 |  |
|  | Rated lightning impulse withstand voltage, peak value | kV | 110 |  |
|  | Circuit breaker withdrawable (yes/no) | - | yes |  |
|  | CB operation |  | Spring-charged motor operated, with provision for manual |  |
|  | CB Operation Preferences (Open/Close) |  | Local, remote and Manual |  |
|  | Short time withstand current | kA | 36 |  |
|  | Momentary withstand and closing and latching current | kA | 97 peak |  |
|  | Rated busbar current | A | 1250/ 2,500 |  |
|  | Rated MV feeders current/ CB rating | A | 1250 & 630 |  |
|  | Rated short time current (3 sec) | kA | 31.5 |  |
|  | Type tested according to IEC 62271 Part 200 including arc classification IAC: AFLR | Yes / No | Yes |  |
|  | Surge Arrestor Switching impulse protective level | kV | 46.2 |  |
|  | Surge Arrestor Lightning impulse protective level | kV | 54 |  |
|  | Conductor material |  | Copper |  |
|  | Conductor shape |  | Rectangular |  |
|  | Conductor insulation |  | Air insulated with porcelain |  |
|  | Minimum clearance Phase-to-earth | Mm | 200 |  |
|  | Minimum clearance Phase-to-phase | Mm | 200 |  |
|  | Standards applied | - | IEC 62271 |  |
|  | Quality control | - | ISO 9001 |  |
|  | Auxiliary Systems and Components |  |  |  |
|  | Earthing Switch |  | Integrated |  |
|  | Instrument Transformers (VT & CT) Accuracy class |  | 0.2S/5P |  |
|  | Protection Relays |  | Digital/microprocessor-based multifunction relays |  |
|  | One common acoustic horn |  | Integrated |  |
|  | Metering (A, V, KWHr, KW, F, KVAR) Include selector switch for reading each phase voltage |  | Integrated with peak demand indications |  |
|  | Interlocks |  | Comprehensive mechanical and electrical interlocks (include door interlock) |  |
|  | Indication lamps for interlocking, opening and closing of circuit breakers ….etc |  | Provide |  |
|  | Switches for local and remote operation Push buttons for open/close operation |  | Provide |  |
|  | Emergency switch |  | Integrated |  |
|  | Anti-condensation Heater |  | Provided |  |

- Circuit breaker： 15 KV, 630 A (Spare to the No. 10 MV Feeder Cubicles CB)

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| Circuit breaker： 24 KV, 630 A |  |  |  |  |
|  | Quantity | set | 5 |  |
|  | Rated system voltage | KV | 15 |  |
|  | Max. system rated voltage | KV | 24 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Current rating | A | 1250 & 630 |  |
|  | Rated short time current | KA | 31.5/40 |  |
|  | Rated short-circuit closing current | KA | 80/100 |  |
|  | Rated peak withstand current | KA | 80/100 |  |
|  | Short time withstands current | KA | 31.5/40 |  |
|  | Rated short-circuit continuous current | S | 3 |  |
|  | Rated breaking current for a single capacitor bank | A | 630 |  |
|  | Rated capacitor back-to-back capacitor bank opening current | A | 400 |  |
|  | 1 minute power frequency withstand voltage | KV | 44 |  |
|  | Withstand voltage for lightning impulses | KV | 110 (After correcting for altitude) |  |
|  | Rated number of short-circuit breaking current interruptions | Times | 30 |  |
|  | Mechanical life | Times | 10000 |  |
|  | Rated sequence of operations |  | O-0.3s-CO-180s-CO |  |
|  | Opening time | Ms | ≤50 |  |
|  | Closing time | Ms | ≤75 |  |
|  | Control voltage | V | DC110 |  |
|  | Closing coil power | W | - |  |
|  | Open coil power | W | - |  |

- 15 KV Transformer incoming cubicle, 2 500 A

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| 15 KV MV switchgear, 2500 A |  |  |  |  |
|  | Manufacturer | - |  |  |
|  | Origin of manufacture |  |  |  |
|  | Quantity | set |  |  |
|  | Type | - | Metal-clad, metal-enclosed, indoor floor-mounting, free-standing cubicle |  |
|  | Type of circuit breaker (vacuum, SF6) (Refer item No. 13 for breaker specifications) | - | Vacuum |  |
|  | Protection class indoor panels | IP | 41 |  |
|  | Protection class outdoor panels | IP | 54 |  |
|  | Protection relays (earth fault, overcurrent… etc) | - | Provided |  |
|  | Energy meter | - | Provided |  |
|  | Rated system voltage | KV | 15 |  |
|  | Max. system rated voltage | KV | 24 |  |
|  | Rated power frequency withstand voltage, rms value, kV during 1 mn | KV | 44 |  |
|  | Rated lightning impulse withstand voltage, peak value | KV | 110 |  |
|  | Circuit breaker withdrawable (yes/no) | - | yes |  |
|  | CB operation |  | Spring-charged motor operated, with provision for manual |  |
|  | Short time withstand current | KA | 36 |  |
|  | Momentary withstand and closing and latching current | KA | 97 peak |  |
|  | Rated busbar current | A | 2,500 |  |
|  | Rated TR Transformer Incoming Bay current | A | 1,250 |  |
|  | CB current Rating | A | 1,250 |  |
|  | Rated short time current (3 sec) | kA | 31.5 |  |
|  | Type tested according to IEC 62271 Part 200 including arc classification IAC: AFLR | Yes / No | Yes |  |
|  | Surge Arrestor Switching impulse protective level | kV | 46.2 |  |
|  | Surge Arrestor Lightning impulse protective level | kV | 54 |  |
|  | Conductor material |  | Copper |  |
|  | Conductor shape |  | Rectangular |  |
|  | Conductor insulation |  | Air insulated with porcelain |  |
|  | Minimum clearance Phase-to-earth | mm | 200 |  |
|  | Minimum clearance Phase-to-phase | mm | 200 |  |
|  | Standards applied | - | IEC 62271 |  |
|  | Quality control | - | ISO 9001 |  |
|  | Auxiliary Systems and Components |  |  |  |
|  | Earthing Switch |  | Integrated |  |
|  | Instrument Transformers (CT & VT) Accuracy class |  | 0.2S/5P |  |
|  | Protection Relays (Each cubicle must include transformer and bus bar protection relays) |  | Digital/microprocessor-based multifunction relays |  |
|  | One common signaling combination relay for ten (10) signals |  | integrated |  |
|  | One common annunciator table for ten (10) signals |  | integrated |  |
|  | One common acoustic horn |  | Integrated |  |
|  | Metering (A, V, KWHr, KW, F, KVAR) Include selector switch for reading each phase voltage |  | Integrated with peak demand indications |  |
|  | Indication lamps for interlocking, opening and closing of circuit breakers ….etc |  | Provide |  |
|  | Switches for local and remote operation Push buttons for open/close operation |  | Provide |  |
|  | Emergency switch |  | Integrated |  |
|  | Interlocks |  | Comprehensive mechanical and electrical interlocks |  |
|  | Anti-condensation Heater |  | Provide |  |

- Circuit breaker： 15 KV, 1250 A (Spare to the No. 12 MV transformer incoming Cubicle CB)

| No. | Item | Unit | Employer requirements | Vendor data |
| --- | --- | --- | --- | --- |
| Circuit breaker： 24 KV, 1250 A |  |  |  |  |
|  | Quantity | set | 3 |  |
|  | Rated system voltage | KV | 15 |  |
|  | Max. system rated voltage | KV | 24 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Current rating | A | 1250 |  |
|  | Rated short time current | KA | 31.5/40 |  |
|  | Rated short-circuit closing current | KA | 80/100 |  |
|  | Rated peak withstand current | KA | 80/100 |  |
|  | Short time withstands current | KA | 31.5/40 |  |
|  | Rated short-circuit continuous current | S | 3 |  |
|  | Rated breaking current for a single capacitor bank | A | 630 |  |
|  | Rated capacitor back-to-back capacitor bank opening current | A | 400 |  |
|  | 1 minute power frequency withstand voltage | KV | 44 |  |
|  | Withstand voltage for lightning impulses | KV | 110 (After correcting for altitude) |  |
|  | Rated number of short-circuit breaking current interruptions | Times | 30 |  |
|  | Mechanical life | Times | 10000 |  |
|  | Rated sequence of operations |  | O-0.3s-CO-180s-CO |  |
|  | Opening time | ms | ≤50 |  |
|  | Closing time | ms | ≤75 |  |
|  | Control voltage | V | DC110 |  |
|  | Closing coil power | W | - |  |
|  | Open coil power | W | - |  |

- Current transformers： 15 KV

| No. | Item | Unit | Employer requirements | Vendor data |
| --- | --- | --- | --- | --- |
| Current transformers： 15 KV |  |  |  |  |
|  | Type |  | Single pole molded type |  |
|  | Installation |  | Indoor |  |
|  | Quantity | set | 20 |  |
|  | Rated primary current | A | 150-300 |  |
|  | Preparatory level combinations |  | 0.5/5P20/5P20/5P20 |  |
|  | Rated capacity | VA | 30/30/30VA/30VA |  |
|  | Rated short-time thermal current | KA | 31.5/4S |  |
|  | Rated dynamic and stable current | KA | 80 |  |
|  | Rated secondary current | A | 1 |  |
|  | Insulation level | kV | 17.5/38/95(After correcting for altitude |  |

- Voltage transformer: 15 KV

| No. | Item | Unit | Employer requirements | Vendor data |
| --- | --- | --- | --- | --- |
| Voltage transformer: 15 KV |  |  |  |  |
|  | Type |  | Single pole molded type |  |
|  | Quantity | Set | 10 |  |
|  | Installation |  | Indoor |  |
|  | Rated primary voltage | KV | 15/ √3 |  |
|  | Rated secondary voltage | KV | Incoming line PT: 0.11/√3/0.11/√3/0.11/3 Feeder PT：0.11/√3 Busbar PT：0.11/√3/0.11/√3/0.11/3 |  |
|  | Accuracy level |  | Incoming line PT: 0.2/1.0/3P Feeder PT：1.0 Busbar PT：0.2/1.0/3P |  |
|  | Rated output | VA | Incoming line PT: 50/50/50 Feeder PT：50 Busbar PT：50/50/50 |  |
|  | Extreme output | VA | Incoming line PT: 100/100/100 Feeder PT：100 Busbar PT：100/100/100 |  |
|  | Rated insulation level | KV | 17.5/38/95(After correcting for altitude |  |
|  | Pollution level |  | Indoor Class |  |

- 15 KV Bus Coupler

| No. | Item | Unit | Description | Vendor data |
| --- | --- | --- | --- | --- |
| 15 KV MV Bus coupler Cubicle, 2,500 A |  |  |  |  |
|  | Manufacturer | - |  |  |
|  | Origin of manufacture |  |  |  |
|  | Quantity | set | 2 |  |
|  | Type | - | Metal-clad, metal-enclosed, indoor floor-mounting, free-standing cubicle |  |
|  | Material thickness | mm | Min. 2 – 3 mm |  |
|  | Type of circuit breaker | - | Vacuum |  |
|  | Protection class indoor panels | IP | 41 |  |
|  | Protection relays (earth fault, overcurrent… etc) | - | Provided |  |
|  | Energy meter | - | Provided |  |
|  | Rated system voltage | kV | 15 |  |
|  | Max. system rated voltage | kV | 24 |  |
|  | Rated power frequency withstand voltage, rms value, kV during 1 mn | kV | 44 |  |
|  | Rated lightning impulse withstand voltage, peak value | kV | 110 |  |
|  | Circuit breaker withdrawable (yes/no) | - | yes |  |
|  | Operation |  | Spring-charged motor operated, with provision for manual charging. |  |
|  | Short time withstand current | kA | 36 |  |
|  | Momentary withstand and closing and latching current | kA | 97 peak |  |
|  | Rated busbar current | A | 2,500 |  |
|  | Breaker current rating | A | 1250 |  |
|  | Rated short time current (3 sec) | kA | 31.5 |  |
|  | Type tested according to IEC 62271 Part 200 including arc classification IAC: AFLR | Yes / No | Yes |  |
|  | Surge Arrestor Switching impulse protective level | kV | 46.2 |  |
|  | Surge Arrestor Lightning impulse protective level | kV | 54 |  |
|  | Conductor material |  | Copper |  |
|  | Conductor shape |  | Consistent with switchgear |  |
|  | Conductor insulation |  | Air insulated with porcelain |  |
|  | Minimum clearance Phase-to-earth | Mm | 200 |  |
|  | Minimum clearance Phase-to-phase | Mm | 200 |  |
|  | Standards applied | - | IEC 62271 |  |
|  | Quality control | - | ISO 9001 |  |
|  | Auxiliary Systems and Components |  |  |  |
| - 1 | Earthing Switch |  | Integrated |  |
|  | Instrument Transformers (CT & VT) Accuracy class |  | 0.2S/5P |  |
|  | Protection Relays |  | Digital/microprocessor-based multifunction relays |  |
|  | Interlocks |  | Comprehensive mechanical and electrical interlocks |  |
|  | Anti-condensation Heater |  | Provided |  |

- Walkie-Talkie radio repeaters for communication between the power plants and substations, as well as for line men

| No. | Item | Unit | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| Walkie-Talkie radio repeater for communication between the power plants and substations, as well as for line men |  |  |  |  |
|  | Manufacturer |  | Motorola, brand code SLR5500 or equivalent |  |
|  | Quantity | set | 2 |  |
|  | Receiving Frequency | MHz | 154 |  |
|  | Transmitting Frequency | MHz | 149.450 |  |
|  | Operating Mode | - | Analog FM, Digital (e.g., DMR), or Mixed-Mode |  |
|  | Output Power | W | Typically 25- 50 (or higher, depending on distance) |  |
|  | Channel Capacity | No | Sufficient for dedicated channels/talk groups for different teams |  |
|  | Channel Spacing | kHz | 12.5 kHz or better (for narrowband compliance) |  |
|  | Frequency Stability | ppm | ± 1.0 ppm or better |  |
|  | Receiver Sensitivity | µV & dB | Analog: 0.25 µV at 12dB SINAD or better; Digital: 0.25 µV at 5% BER or better |  |
|  | Selectivity | dB | 70 or better |  |
|  | Intermodulation Rejection | dB | 70 or better |  |
|  | Spurious Emissions | dBm | -70 or better (Transmitter & Receiver) |  |
|  | Antenna Interface | - | N-type connector |  |
|  | Duplexer | - | High-quality, low-loss duplexer (internal or external) |  |
|  | Power Supply | - | AC Mains (with 300 Ah battery backup for power outages) |  |
|  | Power Supply voltage | V | 220 – 240 |  |
|  | Operating Temperature | °C | -20 to +60 or wider (depending on installation environment) |  |
|  | Humidity Protection | % | Up to 95% non-condensing |  |
|  | Ingress Protection (IP Rating) | No | IP 54 or better (depending on installation environment) |  |
|  | Mounting | inch | Rack mountable (19-inch standard) or wall/pole mountable |  |
|  | Controller Interface | - | For external repeater controller (if advanced features needed) |  |
|  | Remote Management | - | SNMP, web-based interface, or proprietary software (optional) |  |
|  | Lightning Protection | - | Built-in or provision for external surge protection |  |
|  | Grounding | - | Proper grounding lugs and instructions provided |  |
|  | Automatic Gain Control (AGC) | - | Built-in AGC |  |
|  | CTCSS/DCS Tone Support | - | Wide range of CTCSS and DCS codes supported |  |
|  | Voice Storage | Yes | For recording transmissions |  |
|  | Link Interface (Optional) | Yes | For connecting to other repeaters or communication systems (e.g., via IP) |  |
|  | Compliance/Standards | - | Relevant regulatory standards (e.g., FCC, ETSI), safety standards |  |

- long range two-way radio walkie talkie

| No. | Item | Unit | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| long range two-way radio walkie talkie |  |  |  |  |
|  | Model |  | Arcshell or equivalent brand, portable type |  |
|  | Quantity | set | 20 |  |
|  | Licensing | - | Not required |  |
|  | Max Power Output | Watts | Up to 50+ (handhelds typically 2-5) |  |
|  | Typical Range (Ideal Conditions) | Km | 10 Km |  |
|  | Typical Range (Real-World) | - | reliable for longer distances |  |
|  | Receiving Frequency | MHz | 149.450 |  |
|  | Transmitting Frequency | MHz | 154 |  |
|  | Antenna | - | fixed, with options for external antennas |  |
|  | Receiver Sensitivity | - | Excellent |  |
|  | Durability/IP Rating | No | rugged with high IP ratings |  |
|  | Battery Life | - | Long (> 5 hrs.) |  |
|  | Spare Battery |  | 30 |  |
|  | Battery charger | Qty | 30 |  |

- long range car mounted base station walkie talkie radio

| No. | Item | Unit | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
| long range car mounted base station walkie talkie radio |  |  |  |  |
|  | Type/ Model |  |  |  |
|  | Quantity | set | 30 |  |
|  | Receiving Frequency | MHz | 149.450 |  |
|  | Transmitting Frequency | MHz | 154 |  |
|  | Power Output | Watts | Typically 25 to 50+ |  |
|  | Power Supply | - | AC Mains (with 300 Ah battery backup for power outages) |  |
|  | Power Supply voltage | V | 220 – 240 |  |
|  | Channel Capacity | No | Programmable for numerous channels/talk groups |  |
|  | Channel Spacing | kHz | Typically 12.5 or better (for narrowband compliance) |  |
|  | Frequency Stability | Ppm | ± 1.5 or better |  |
|  | Receiver Sensitivity | µV & dB | 0.25 µV or better for 12dB SINAD (Analog); 0.25 µV for 5% BER (Digital) |  |
|  | Selectivity | dB | 70 or better |  |
|  | Intermodulation Rejection | Db | 70 or better |  |
|  | Spurious Emissions | DBm | -70 or better |  |
|  | Antenna Connector | - | Typically SO-239 (PL-259) or N-type |  |
|  | External Antenna Requirement | - | Yes, for long range |  |
|  | Power Supply | V | 12 DC (vehicle battery) |  |
|  | Operating Temperature | °C | Wide range (e.g., -20 to +60 or wider) |  |
|  | Durability/Ruggedness | - | Mobile-grade construction, often with vibration and shock resistance |  |
|  | Microphone Connector | - | Standard microphone connector (e.g., RJ45, 8-pin round) |  |
|  | Mounting Options | - | Bracket for under-dash or console mounting (Car mounted) |  |
|  | Digital Capabilities | - | DMR, P25, etc. ( |  |
|  | Remote Head/Control | - | Yes, allows control of the radio when the main unit is mounted in a less accessible location. |  |
|  | Compliance/Standards | - |  |  |

- Battery bank with battery charger

| No. | Item | Unit | Design requirements |  |
| --- | --- | --- | --- | --- |
| Battery bank and battery charger |  |  |  |  |
|  | Quantity | Set (Batt storage + charger) | 15 |  |
|  | Application |  | Substation DC system (Backup power) |  |
|  | Battery Configuration |  | 60 cells × 2 V in series = 120 V DC, minimum 500 Ah |  |
|  | Battery Type |  | NiCd |  |
|  | DC Output Voltage | V | Adjustable 108 V – 138 V DC (for float and boost) |  |
|  | DC Output Current | A | 20–25 A minimum (10–12% of battery capacity) |  |
|  | Charging Modes |  | Float charging, Boost (equalization) |  |
|  | AC Input Voltage | V | 380 V AC three-phase |  |
|  | Control |  | Digital controller with programmable charging profiles |  |
|  | Cooling |  | Forced air (fan cooled) |  |
|  | Protections |  | Overvoltage, Overcurrent, Short-circuit, Reverse polarity, etc. |  |
|  | Display/Monitoring |  | LCD display; RS485 communication |  |
|  | Redundancy Option |  | N+1 modular configuration |  |
|  | Standards Compliance |  | IEC 62040-1, IEC 60146, EN 61000 (EMC), CE |  |
|  | Installation Location |  | Indoor (panel mounted or rack type) |  |
|  | battery bank capacity | KWh |  |  |
|  | battery charger capacity | A | 150 |  |

- Protection systems (Relays)

The following list details the existing protection relays currently installed in national grid substations. The Ministry of Energy and Mines (MOEM) requires that bidders propose identical or technically equivalent relays as part of their offer. Furthermore, MOEM welcomes comprehensive protection system solutions, including proposals for entirely new, separate protection panels incorporating modern relays and integrated monitoring devices for 66 KV and 132 KV systems. MOEM will later review both submitted options and inform the awarded bidder of its decision.

- Multifunction data recording and communication module

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Multifunction data recording and communication module |  |  |  |  |
|  | Type |  | MC-R |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 10 |  |
|  | Reference standards |  | IEC 870-5, IEC 255, 801; CEI 41-1; IEEE C37; CE |  |
|  | Average power supply consumption | VA | 2.5 |  |
|  | Output relays |  | Rating 5A; 250V AC Max switching power = 1250VA Max switching current = 5A(resistive) Max switching voltage = 250 AC – 110VDC Max make current = 0.2A, 110V DC, L/R=40ms |  |

- Digital multifunction transformer differential protection relay

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Digital multifunction transformer differential protection relay |  |  |  |  |
|  | Type |  | MD32-T |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 20 |  |
|  | Reference standards |  | IEC 255, IEC 1000; IEEE C37; CE directive |  |
|  | Max power supply consumption | VA | 8.5 |  |
|  | Output relays |  | Rating 5A; 380V AC A.C. resistive switching = 1100W (380V max) Make 30A (peak) 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (1000.000 op.) |  |

- Microprocessor overcurrent and earth fault protection relay + auto reclose

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Microprocessor overcurrent and earth fault protection relay + auto reclose |  |  |  |  |
|  | Type |  | IM30-AE |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 20 |  |
|  | Reference standards |  | IEC 255, IEC 1000; IEEE C37; CE directive |  |
|  | average power supply consumption | VA | 8.5 |  |
|  | Output relays |  | Rating 5A; 380V AC A.C. resistive switching = 1100W (380V max) Make 30A (peak) 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (100.000 op.) |  |

- Microprocessor overcurrent and differential earth fault protection relay + auto reclose

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Microprocessor overcurrent and differential earth fault protection relay + auto reclose |  |  |  |  |
|  | Type |  | IM30-DRE |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 30 |  |
|  | Reference standards |  | IEC 255, IEC 1000; IEEE C37; CE directive |  |
|  | average power supply consumption | VA | 10 |  |
|  | Output relays |  | Rating 5A; 380V AC A.C. resistive switching = 1100W (380V max) Make 30A (peak) 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (1000.000 op.) |  |

- Modular low impedance bus bar protection

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Modular low impedance bus bar protection |  |  |  |  |
|  | Type |  | M-LIB3 |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 5 |  |
|  | Reference standards |  | IEC 255, IEC 1000; IEEE C37; CE directive |  |
|  | average power supply consumption | VA | 8.5 |  |
|  | Output relays |  | Rating 5A; 380V AC A.C. resistive switching = 1100W (380V max) Make 30A (peak) 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (1000.000 op.) |  |

- Relays interfacing program

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Relays interfacing program |  |  |  |  |
|  | Type |  | MSCom |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 5 |  |

- Zero sequence overcurrent relay

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Zero sequence overcurrent relay |  |  |  |  |
|  | Type |  | UBO/A |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 5 |  |
|  | Reference standards |  | CEI 41-1; IEC 255 ; BS 142 |  |
|  | average power supply consumption | VA | 3.5 |  |
|  | Output relays |  | Rating 5A; 380V AC A.C. resistive switching = 1100W (380V max) Make 30A (peak) 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (100.000 op.) |  |

- High impedance deferential Relays

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| High impedance deferential Relays |  |  |  |  |
|  | Type |  | UBO/ATR |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 5 |  |
|  | Reference standards |  | CEI 41-1; IEC 255; BS 142 |  |
|  | average power supply consumption | VA | 3.5 |  |
|  | Output relays |  | Rating 5A; 380V AC A.C. resistive switching = 1100W (380V max) Make 30A (peak) 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (100.000 op.) |  |

- Lock-out Relays

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Lock-out Relays |  |  |  |  |
|  | Type |  | RB4 |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 10 |  |
|  | Reference standards |  | CEI 41-1/IEC 255 |  |
|  | Pick-up power supply consumption | VA | Less than or equal 15 |  |
|  | Output relays |  | Breaking capacity (1000,000 op) 0.5A 125V DC L/R =40ms 10A 110V AC cosfi=0.7 4A 380V AC cosfi= 0.7 Making and carry capacity: 80A 1sec |  |

- Trip circuit supervision relay

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Trip circuit supervision relay |  |  |  |  |
|  | Type |  | RCA |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 40 |  |
|  | Reference standards |  | IEC 255,801,805; CEI 41-1-IEEE C37 |  |
|  | average power supply consumption | VA | 3.5 |  |
|  | Output relays |  | Two S.P.D.T Rating current at 5A; 380V AC Rated A.C. resistive switching power= 1100W (380V max) Make 30A (peak) X 0.5sec. Break = 0.3A, 110Vcc, L/R=40 ms (100.000 op.) |  |

- The DLP digital relaying system for single and three pole tripping application

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| The DLP digital relaying system for single and three pole tripping application |  |  |  |  |
|  | Type |  | ---- |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 10 |  |
|  | Reference standards |  |  |  |
|  | average power supply consumption | VA |  |  |
|  | Output relays |  |  |  |

- DLP1112KDH

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| DLP1112KDH (21+67N+79+27) |  |  |  |  |
|  | Type |  | DLP1112KDH |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 12 |  |
|  | Reference standards |  |  |  |
|  | average power supply consumption | VA |  |  |
|  | Output relays |  |  |  |

- Multifunction microprocessor synchrocheck relay

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Multifunction microprocessor synchrocheck relay |  |  |  |  |
|  | Type |  | SCM21 |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 10 |  |
|  | Reference standards |  | IEC 255,801,805; CEI 41-1-IEEE C37; CE |  |
|  | average power supply consumption | VA | 8.5 |  |
|  | Output relays |  | Rating 5 A; 380 V AC A.C. resistive switching = 1100 W (380 V max) Make 30 A (peak) 0.5 sec. Break = 0.3 A, 110 Vcc, L/R=40 ms (100.000 op.) |  |

- Matrix Interfacing module

| No. | Item | Unit | Specification | Vendor data |
| --- | --- | --- | --- | --- |
| Matrix Interfacing module |  |  |  |  |
|  | Type |  | MX7-5 |  |
|  | Manufacturer |  | MICROELETTRICA or equivalent |  |
|  | Country of origin |  | Italy |  |
|  | Quantity | Set | 5 |  |
|  | Reference standards |  | IEC 255,801,805; CEI 41-1-IEEE C37; CE |  |
|  | average power supply consumption | VA | 8.5 |  |
|  | Output relays |  | Rating 5 A; 250 V AC Max switching power= 1250 VA |  |

- Protection panel 66 KV &132 KV (Optional: If complete protection system solution is also offered)

| No. | Item | Unit | Design requirements | Vendor data |
| --- | --- | --- | --- | --- |
|  | 66 KV Line Protector |  |  |  |
|  | Manufacturer |  |  |  |
|  | Origin of manufacturer |  |  |  |
|  | Quantity | Set | 12 |  |
|  | Relay |  | Microprocessor based numeric |  |
|  | Standards |  | IEC 60255 |  |
|  | Maximum ambient temperature for rated accuracy | 0C | 55 |  |
|  | Max. Humidity | % | 80 |  |
|  | Rated Frequency | Hz | 50 |  |
|  | CT secondary current | A | 1 & 5 |  |
|  | Electromagnetic compatibility test |  | IEC 60255-5 ，IEC 60255-6 IEC 60255-22-3, IEC 60255-22-4, IEC 60068-2 |  |
|  | Fault Monitoring System |  |  |  |
| 1 | Manufacturer |  |  |  |
| 2 | Type |  |  |  |
| 3 | Origin of manufacture |  |  |  |
| 4 | Architecture complete separate system shall consist of a fault monitoring and disturbance recorder system (FMS), which shall cover the entire Plant |  |  |  |
|  | Protection and Control Systems |  |  |  |
| 1 | Relays type |  | Digital |  |
| 2 | Contact rating - make and carry for 0.2 s | VA |  |  |
| 3 | Protection class of protection panels installed indoors in an air-conditioned environment |  |  |  |
| 4 | Protection class of protection panels installed outdoors |  | IP 65 |  |
| 5 | Protection class of control panels installed indoors in an air-conditioned environment |  | IP 41 |  |
| 6 | Panels maximum dimensions H x W x D | mm |  |  |
| 7 | Front door material | - | Transparent glass |  |
|  | Auxiliaries |  |  |  |
| 1 | Detailed trip information of electrical protection relays/bay controllers, time stamped at source |  | Yes |  |
| 2 | Detailed information of status of LV/MV switchgear |  | Yes |  |
| 3 | Detailed metering (main and check meter) information |  | Yes |  |
| 4 | Detailed information of fire alarm and security systems |  | Yes |  |
| 5 | Detailed information of control and SCADA system (communication status, equipment status, redundancy status, etc.) |  | Yes |  |
|  | Control / Display Platform |  |  |  |
| 1 | Alarm management with error analysis |  | Yes |  |
| 2 | Management of all Blocks in a single control platform |  | Yes |  |
| 3 | Real time visualization |  | Yes |  |
| 4 | Reaction time between executing command on HMI/operator station to reaction on relay level |  | <1 |  |
| 5 | Comparison between values of different Blocks |  | Yes |  |
| 6 | Configuration of user permission |  | Yes |  |
| 7 | Data export (graphs, file format HTML, CSV) |  | Yes |  |
| 8 | Ability to change internal parameters of the subsystems |  | Yes |  |
| 9 | Ability to monitor the data of the meteorological stations |  | Yes |  |
| 10 | Ability to monitor data of the day-ahead and intra-day weather and solar power forecast system |  | Yes |  |
| 11 | Ability to monitor its own failures |  | Yes |  |
| 12 | Ability to manage permission of works. |  | Yes |  |
| 13 | Ability to inter-operate with interconnected systems |  | Yes |  |
| 14 | Geographical map |  | Yes |  |
| 15 | Layout display of the Project |  | Yes |  |
|  | Metering according to Grid Code |  |  |  |
| 1 | kW/ kVar Hour Meters |  | Yes |  |
| 2 | Number of meters |  | Min 2 |  |
| 3 | Type |  |  |  |
| 4 | Manufacturer |  |  |  |
| 5 | Applicable standards |  | IEC 62053-21 IEC 62053-22 IEC 62053-23 |  |
| 6 | Tested according to Grid Code |  | Yes |  |
| 8 | Peak demand indicator (resettable) |  | Yes |  |
| 9 | Impulse rate |  | 1.2/50μs |  |
| 10 | Protection degree of metering panel | IP | IP 42 |  |
| 11 | Data storage facility | GB | 100 |  |
| 12 | Type of protocol |  |  |  |

PANEL MECHANICAL CHARACTERISTICS:

| ITEM | DESCRIPTION | PARAMETER |
| --- | --- | --- |
| 1 | TYPE |  |
| 2 | DIMESION | 2260*800*800 (H*W*D) |
| 3 | COLOR | EXTERIOR: RAL7035 INTERIOR: RAL7035 |
| 4 | MATERIAL | SHEET STEEL |
| 5 | PLATE THICKNESS | >2mm |
| 6 | MOUNTING | FLOOR MOUNTING, BOTTOM ENTRY OF POWER AND MULTI-CORE CABLES |
| 7 | EARTH BAR | COPPER STRIP: 485(L)×25(W)×4(D)mm |

- MV Cables and Termination tool kit

- 240 mm2 15 KV MV CABLE

| No. | Item | Unit | Design requirements |  | Data by Vendor |
| --- | --- | --- | --- | --- | --- |
| 15KV MV CABLES |  |  |  |  |  |
|  | Manufacturer | - |  |  |  |
|  | Type | - |  |  |  |
|  | Origin of manufacture | - |  |  |  |
|  | Rated voltage | kV | 15 |  |  |
|  | Max. rated voltage | kV | 24 |  |  |
|  | Number of cores |  | Single |  |  |
|  | Insulation | - | XLPE |  |  |
|  | Conductor material | - | copper |  |  |
|  | Cross section | mm2 | 240 |  |  |
|  | Material of metallic screen | - | Vendor Data |  |  |
|  | Overall diameter (D) | mm | Vendor Data |  |  |
|  | Minimum bending radius | x D | Vendor Data |  |  |
|  | Total cable length | m | 1000 |  |  |
|  | Maximum conductor temperature normal operation | 0C | 90 |  |  |
|  | Maximum permissible short circuit conductor temperature | 0C | 250 |  |  |
|  | Nominal thickness of insulation at rated voltage | mm | 5.5 |  |  |
|  | Weight | kg/m | Vendor Data |  |  |
| 15KV Termination Kit |  |  |  |  |  |
|  | Rated power frequency withstand voltage, rms value, kV during 1 mn | kV | 44 |  |  |
|  | Rated lightning impulse withstand voltage, peak value | kV | 110 |  |  |
|  | Manufacturer |  |  |  |  |
|  | Type of Kit |  |  |  |  |  |
|  | Quantity | Three | 1000 |  |  |  |
| 20.1 | --Outdoor | Heat-shrinkable, Qty 500 |  |  |  |
| 20.2 | --Indoor | Heat-shrinkable, Qty 500 |  |  |  |
|  | Standards applied | IEC 60502 |  |  |  |
|  | Quality control | ISO 9001 |  |  |  |
|  | Cable lugs |  |  |  |  |
|  | Quantity | Three phase set |  | 500 for 240 mm2 cable 500 for 120 mm2 cable |  |
|  | Type | - |  | Tabular |  |
|  | HV Cable stripping tool |  |  |  |  |
|  | Quantity |  |  | 4 |  |
|  | Cable lug compressing tool |  |  |  |  |
|  | Quantity |  |  | 4 |  |

- 120 mm2 15 KV MV CABLE

| No. | Item | Unit | Design requirements | Data by Vendor |
| --- | --- | --- | --- | --- |
| 15KV MV CABLES |  |  |  |  |
|  | Manufacturer | - |  |  |
|  | Type | - |  |  |
|  | Origin of manufacture | - |  |  |
|  | Rated voltage | kV | 15 |  |
|  | Max. rated voltage | kV | 24 |  |
|  | Number of cores |  | Single |  |
|  | Insulation | - | XLPE |  |
|  | Conductor material | - | copper |  |
|  | Cross section | mm2 | 120 |  |
|  | Material of metallic screen | - | Vendor Data |  |
|  | Overall diameter (D) | mm | Vendor Data |  |
|  | Minimum bending radius | x D | Vendor Data |  |
|  | Total cable length | m | 1000 |  |
|  | Maximum conductor temperature normal operation | 0C | 90 |  |
|  | Maximum permissible short circuit conductor temperature | 0C | 250 |  |
|  | Nominal thickness of insulation at rated voltage | mm | 5.5 |  |
|  | Weight | kg/m | Vendor Data |  |
|  | Quality control | ISO 9001 |  |  |

- 6MVA Power Transformers

- 6MVA Power Transformer Specifications

The transformers are required to be supplied with all required accessories and manufacturers (or representatives) to witness commissioning.

| Sr.No | Description | Design requirement | Vendor data |
| --- | --- | --- | --- |
|  | Rating in KVA | 6000 |  |
|  | Name of the manufacturer |  |  |
|  | Country of origin |  |  |
|  | Installation | Outdoor |  |
|  | Voltage ratio | 66000/15000 volts |  |
|  | Frequency | 50 Hz |  |
|  | Quantity | 6 |  |
|  | Type of insulation | Three phase mineral oil immersed |  |
|  | Reference standard | IEC 60076/IEC 60296 |  |
|  | Core material | CRGO |  |
|  | Winding material | Electrolytic grade copper |  |
|  | Method of connection |  |  |
|  | - H.V Winding | star |  |
|  | - L.V winding | Delta |  |
|  | - Connection Symbol | YNd11 |
|  | Method of cooling | ONAN |  |
|  | Carrier type | Rail and roller |  |
|  | Maximum Temperature Rise |  |  |
|  | - Oil | 50 0C (47.5 0C with altitude correction |  |
|  | - Winding | 55 0C (52.5 0C with altitude correction |  |
|  | Insulation class | Class A |  |
|  | NGR, Surge arrestor, differential relay | Vendor to supply |  |
|  | Winding and oil temperature sensors | Integrated |  |
|  | CT details | HV phase LV Phase …… etc. |  |
|  | CT Class | 5P20 |  |
|  | Bushing type |  |  |
|  | Creepage distance | 31 mm/KV |  |
|  | Service altitude | 2500 meters |  |
|  | a) Core loss to watts at normal voltage & frequency (max) |  |  |
|  | b) Full load losses at 75 0C at principal tap (max) |  |  |
|  | Maximum flux density at rated condition at principal tap | 1.72 Tesla |  |
|  | Maximum current density at principal tap | 3.50 A/mm2 |  |
|  | Type of Tap changer | On load tap change (OLTC) + 12.5 to -7.5% in step of 1.25% |  |
|  | Tap changer manufacturer |  |  |
|  | Non-cumulative overload capacity after the transformer has reached steady temperature on continuous operation at rated load | 110% for continuous operation |  |
|  |  | 125% for 15 minutes |  |
|  |  | 140% for 5 minutes |  |
|  | Efficiency At 75 0C at |  |  |
|  | a) Unity P.F & (b) 0.8 P.F. | (a) (b) |  |
|  | i)100 % load | 99.06% 98.83% |  |
|  | ii) 75 % load | 99.23% 99.03% |  |
|  | iii) 50% load | 99.35% 99.19% |  |
|  | Regulation at |  |  |
|  | a) unity P.F. | 1.15% |  |
|  | b)0.8 P.F. at 75 0C | 5.61% |  |
|  | % Impedance at 75 0C | 8.00% (Sub. To ± IEC Tol) |  |
|  | Insulation level: |  |  |
|  | Impulse | 325/125 KVp |  |
|  | Power Frequency Voltage | 140/50 KVrms |  |
|  | Terminal arrangement |  |  |
|  | HV side | Bare Bushing |  |
|  | LV side | Cable Box |  |
|  | Approximate Weight of |  |  |
|  | - Core & Winding |  |  |
|  | b)Tank & fittings |  |  |
|  | c)Oil |  |  |
|  | d)Total Weight |  |  |
|  | e)Oil qty. in Lit. |  |  |

- Equipment Documentation

(Awarded bidder to submit necessary documents before the start of manufacturing)

Equipment documentation

datasheets

type test certificates (safety and performance)

type test reports (safety and performance)

FAT schedules (As client will attend FAT at manufacturers premises to witness), Inspection Test Plans (ITP) and reports

installation and operation manuals

Schematic drawings

Product warranties

Other warranties

Other equipment: datasheets

Other equipment: type test certificates

Other equipment: installation and operation manuals

All equipment: End of line test and factory acceptance test (FAT) protocols

Calibration certificates of all calibrated equipment

Configuration and setting manuals

Software

List of which equipment using which serial number was installed where

Default settings of any equipment that require manual settings. The configuration files shall be documented properly in order to assess the purpose and recommended default setting of each value. The documentation shall be suitable to directly configure any spare, replacement or additional equipment of the same type. These shall include, but not be limited to: Conventional protection devices, Heating, ventilation and air conditioning.

………. And others.

4. Drawings

[If documents shall be included, insert the following List of Drawings, separately for each Lot]

| List of Drawings |  |  |
| --- | --- | --- |
| ##### Drawing Nr. | Drawing Name | Purpose |

5. Inspections and Tests

The following inspections and tests shall be performed: Unit testing, Integration testing, Functional testing, Acceptance testing, Performance testing, Smoke testing and other relevant test for each Lot.